## Coils-Coll.
|  |  | ELECTRICAL TESTS OF DIPOLES | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[9 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[9 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO |  | CONTRACT NUMBER : F302 |  |  | YT111 | 10.8964 | Magnet | 6.1471 | 6147.111 | 6074.2204 | 10 | 0.138 | 24.9 |  | 0.274 | 99.5
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  |  | YT112 | 10.7441 | Aperture1 | 3.0657 | 3065.682 | 3029.33 | 100 | 1.34 | 24.8 |  | 2.61 | 99.6
[8 empty] | YT121 | 10.8441 | Aperture2 | 3.081 | 3081.05 | 3081.05 | 1000 | 12.5 | 25.1 |  | 23.7 | 101
COMPONENT NAME : |  |  | Collared Coils |  |  |  |  | YT122 | 10.9634 | Apt1 Pup | 1.5112 | 1511.214 | 1493.2945
CERN PART NUMBER : |  |  | HCMB__A001 |  | Serial Number : |  | 000001 | YT211 | 10.8224 | Apt1 Plw | 1.5543 | 1554.253 | 1535.8231 | 10 | 0.195 | 49.9 |  | 0.275 | 199
[8 empty] | YT212 | 10.902 | Apt2 Pup | -4.52e-07 | -0.000452 | -0.00044664 | 100 | 1.87 | 49.7 |  | 2.62 | 199
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 16 to 18 |  | TEST NUMBER : |  | 16 to 18 | YT221 | 10.868 | Apt2 Plw | 3.0806 | 3080.587 | 3044.0583 | 1000 | 17.2 | 50.3 |  | 23.9 | 203
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number | YT222 | 10.9289
[14 empty] | 10 | 0.138 | 24.9 |  | 0.195 | 49.8
NAME OF TEST OPERATOR: |  |  | Angelo Pavese | [10 empty] | 100 | 1.34 | 24.8 |  | 1.87 | 49.7
NAME OF RESPONSIBLE: |  |  | Bruno Caserza | [10 empty] | 1000 | 12.4 | 25.1 |  | 17.1 | 50.3
DATE OF TEST : |  |  | 2001-02-09 |  | TIME : |  | 0
[14 empty] | 10 | 0.276 | 99.8
[14 empty] | 100 | 2.61 | 99.6
[14 empty] | 1000 | 23 | 101
R[dc] of the Poles
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 23 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 42 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1545 | 1540 |  | 1544 | 1542
Poles [20°C] |  | * | 1527.59 | 1522.64 |  | 1526.6 | 1524.62
D1 & D2 |  | * | 3085 | mW |  | 3086 | mW
Magnet |  |  | * | 6172 | mW
R[dc] of the Quench Heaters
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 19.78 | 19.79 |  | 19.82 | 20.03
|  | * | 20.05 | 19.88 |  | 19.83 | 20.09
Capacitance
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 280 | nF |  | 280 | nF
D1 & D2 | --> Masse |  | 380 | nF |  | 380 | nF
Magnet | --> Masse |  | * | 420 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 13.55 | 13.54 |  | 13.53 | 13.54
|  | (Q) | 0.53 | 0.54 |  | 0.53 | 0.54
D1 & D2 |  | (L) | 40.9 | mH |  | 40.85 | mH
|  | (Q) | 0.81 |  |  | 0.81
Magnet |  |  | (L) | 87.42 | mH
|  |  | (Q) | 0.86
INDUCTANCE L/Q[100Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 13.28 | 13.28 |  | 13.28 | 13.27
|  | (Q) | 3.67 | 3.67 |  | 3.67 | 3.67
D1 & D2 | * | (L) | 40.05 | mH |  | 39.99 | mH
|  | (Q) | 4.57 |  |  | 4.58
Magnet | * |  | (L) | 85.55 | mH
|  |  | (Q) | 4.63
INDUCTANCE L/Q[1.0KHz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 9.94 | 9.9 |  | 9.92 | 9.9
|  | (Q) | 2.47 | 2.45 |  | 2.46 | 2.46
D1 & D2 | * | (L) | 28.8 | mH |  | 28.66 | mH
|  | (Q) | 2 |  |  | 2.02
Magnet | * |  | (L) | 60.96 | mH
|  |  | (Q) | 1.8
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 5.85 | GW |  | >1000MW
[V=1.0.KV, 30'']
Dipole D2 + QHs D2 ----> Masse *
|  |  |  | 6.15 | GW |  | >1000MW
[V=1.0.KV, 30'']
| QHs D1(8x) D1 |  | *
|  |  |  | 5.2 | GW |  | >1000MW
[V=1.0.KV, 30'']
| QHs D2(8x) D2 |  | *
|  |  |  | 4.02 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 16.3 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 11.6 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 3.1 | µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 2.8 | µA
[V=6.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.6 | µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.4 | µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.1 | µA
[V=3.KV 5']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.1 | µA
[V= 3KV 5']
DISCHARGE TEST
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.99 | 1 |  | 0.99 | 0.99
| Dipoles D1 & D2 [4KV] * |  | 1.79 | mS | * | 1.78 | mS
| Magnet [4KV] |  | * | 2.66 | mS
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION

## P001
ELECTRICAL TESTS OF POLES
|  |  | [ACCEPTANCE TEST] |  | Date : | 2000-10-11
POLE TYPE : |  | MB |  |  | Serial Nr. | P001
Inner Layer Nr. |  | I004 | Cable I Nr. | 01C00003A
Outer Layer Nr. |  | E004 | Cable O Nr. | 02E00213C
INSULATION RESISTANCE
Before splice soldering
INNER LAYER --> OUTER LAYER |  |  |  | 23800 | MW | >1000MW
[V= 1KV 30"]
R[dc] of the Pole
I = | 1 | A
Temp.* : | 20 | °C |  | 1537 | mV
| POLE |  |  | 1537 | mW
| POLE [R20] |  |  | 1537 | mW
R[dc] of the Splice
I = | 30 | A
Temp.* : | 20 | °C |  | 1.941 | mV
| Splice |  |  | 64.7 | µW
INDUCTANCE
[Value from gain phase analyser]
|  |  |  | L | Q
[mH]
| POLE |  | 10Hz | 14.04 | 0.56
|  |  | 100Hz | 13.87 | 4.92
|  |  | 1000Hz | 13.07 | 15.3
DISCHARGE TEST
Whitout Strain
V = 100V/turn |  |  | T | 1050 | µS [Reference Pole]
| POLE | [4KV; 10 puls] | T | 1051 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends]
V = 120V/turn
| POLE |  | C.side T | 1051 | µS
|  |  | N.C. side T | 1051 | µS
[4.8KV; 10 puls]

## I004
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO |  | CONTRACT NUMBER |  | F302
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME : |  |  | INNER LAYER
CERN PART NUMBER : |  |  | HCMB__A011 |  | Serial Number : |  | I004
CERN INSPECTION & TEST PLAN NUMBER: |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | <Yes/No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | Angelo Pavese
NAME OF RESPONSIBLE |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2000-05-12 |  | TIME: |  | 0
Cable "I" Number : |  |  | 01C0003A
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 21 | °C
[5 empty] | 512 | mV
| Inner LAYER |  |  |  | 512 | mW
| Inner LAYER[R20] |  |  |  | 510.0618 | mW
INDUCTANCE | [6 empty] | ITP step 4
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Inner LAYER |  |  | 10Hz
|  |  |  | 100Hz | 1.9 | 2
|  |  |  | 1000Hz | 1.84 | 12
INSULATION RESISTANCE | [6 empty] | ITP step 6
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 19000 | MW
| Right side |  |  |  | 7900 | MW
[V = 500V 30"]
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 5
V = 120Vturn |  |  |  | T | 390 | µS [Reference layer]
| Inner LAYER [1.5KV ; 10puls] |  |  | T | 390 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120Vturn
| Inner LAYER |  |  | C.side T | 394 | µS
| [1.8KV ; 10puls] |  |  | N.C. side T | 394 | µS
LHC/MMS TRACEABILITY INFORMATION

## E004
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO |  | CONTRACT NUMBER |  | F302
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME |  |  | OUTER LAYER
CERN PART NUMBER : |  |  | HCMB__A012 |  | Serial Number : |  | E004
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | <Yes/No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | Angelo Pavese
NAME OF RESPONSIBLE |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2000-05-31 |  | TIME: |  | 0
Cable "O" Number : |  |  | 02E00213C
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 22 | °C
[5 empty] | 1029 | mV
| Outer LAYER |  |  |  | 1029 | mW
| Outer LAYER[R20] |  |  |  | 1021.2386 | mW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Outer LAYER |  |  | 10Hz
|  |  |  | 100Hz | 6.6 | 3.5
|  |  |  | 1000Hz | 6.52 | 27.4
INSULATION RESISTANCE
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 9800 | MW
| Right side |  |  |  | 5400 | MW
[V = 500V 30"]
DISCHARGE TEST
[ Whithout Strain] | [6 empty] | ITP step 5
V = 120V/turn |  |  |  | T | 744 | µS [Reference layer]
| Outer LAYER [3.0KV ; 10puls] |  |  | T | 746 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120V/turn
| Outer LAYER |  |  | C.side T | 748 | µS
|  |  |  | N.C. side T | 748 | µS
[3.0KV ; 10puls]
LHC/MMS TRACEABILITY INFORMATION

## P002
ELECTRICAL TESTS OF POLES
|  |  | [ACCEPTANCE TEST] |  | Date : | 2000-10-11
POLE TYPE : |  | MB |  |  | Serial Nr. | P002
Inner Layer Nr. |  | I001 | Cable I Nr. | 01C00001A
Outer Layer Nr. |  | E001 | Cable O Nr. | 02E00213F
INSULATION RESISTANCE
Before splice soldering
INNER LAYER --> OUTER LAYER |  |  |  | 30000 | MW | >1000MW
[V= 1KV 30"]
R[dc] of the Pole
I = | 1 | A
Temp.* : | 20 | °C |  | 1535 | mV
| POLE |  |  | 1535 | mW
| POLE [R20] |  |  | 1535 | mW
R[dc] of the Splice
I = | 30 | A
Temp.* : | 20 | °C |  | 2.16 | mV
| Splice |  |  | 72 | µW
INDUCTANCE
[Value from gain phase analyser]
|  |  |  | L | Q
[mH]
| POLE |  | 10Hz | 13.73 | 0.55
|  |  | 100Hz | 13.61 | 4.91
|  |  | 1000Hz | 12.9 | 16.3
DISCHARGE TEST
Whitout Strain
V = 100V/turn |  |  | T | 1041 | µS [Reference Pole]
| POLE | [4KV; 10 puls] | T | 1044 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends]
V = 120V/turn
| POLE |  | C.side T | 1058 | µS
|  |  | N.C. side T | 1058 | µS
[4.8KV; 10 puls]

## I001
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO |  | CONTRACT NUMBER |  | F302
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME : |  |  | INNER LAYER
CERN PART NUMBER : |  |  | HCMB__A011 |  | Serial Number : |  | I001
CERN INSPECTION & TEST PLAN NUMBER: |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | <Yes/No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | Angelo Pavese
NAME OF RESPONSIBLE |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2000-05-09 |  | TIME: |  | 0
Cable "I" Number : |  |  | 01C0001A
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 19 | °C
[5 empty] | 507 | mV
| Inner LAYER |  |  |  | 507 | mW
| Inner LAYER[R20] |  |  |  | 508.9339 | mW
INDUCTANCE | [6 empty] | ITP step 4
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Inner LAYER |  |  | 10Hz
|  |  |  | 100Hz | 1.89 | 2
|  |  |  | 1000Hz | 1.83 | 11
INSULATION RESISTANCE | [6 empty] | ITP step 6
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 32000 | MW
| Right side |  |  |  | 14600 | MW
[V = 500V 30"]
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 5
V = 120Vturn |  |  |  | T | 392 | µS [Reference layer]
| Inner LAYER [1.5KV ; 10puls] |  |  | T | 393 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120Vturn
| Inner LAYER |  |  | C.side T | 399 | µS
| [1.8KV ; 10puls] |  |  | N.C. side T | 399 | µS
LHC/MMS TRACEABILITY INFORMATION

## E001
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO |  | CONTRACT NUMBER |  | F302
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME |  |  | OUTER LAYER
CERN PART NUMBER : |  |  | HCMB__A012 |  | Serial Number : |  | E001
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | <Yes/No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | Angelo Pavese
NAME OF RESPONSIBLE |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2000-06-09 |  | TIME: |  | 0
Cable "O" Number : |  |  | 02E00213F
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 25 | °C
[5 empty] | 1026 | mV
| Outer LAYER |  |  |  | 1026 | mW
| Outer LAYER[R20] |  |  |  | 1006.8695 | mW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Outer LAYER |  |  | 10Hz
|  |  |  | 100Hz | 6.64 | 3.5
|  |  |  | 1000Hz | 6.52 | 24.4
INSULATION RESISTANCE
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 10700 | MW
| Right side |  |  |  | 14300 | MW
[V = 500V 30"]
DISCHARGE TEST
[ Whithout Strain] | [6 empty] | ITP step 5
V = 120V/turn |  |  |  | T | 744 | µS [Reference layer]
| Outer LAYER [3.0KV ; 10puls] |  |  | T | 744 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120V/turn
| Outer LAYER |  |  | C.side T | 748 | µS
|  |  |  | N.C. side T | 748 | µS
[3.0KV ; 10puls]
LHC/MMS TRACEABILITY INFORMATION

## P003
ELECTRICAL TESTS OF POLES
|  |  | [ACCEPTANCE TEST] |  | Date : | 2000-10-11
POLE TYPE : |  | MB |  |  | Serial Nr. | P003
Inner Layer Nr. |  | I003 | Cable I Nr. | 01C00002A
Outer Layer Nr. |  | E003 | Cable O Nr. | 02E00213B
INSULATION RESISTANCE
Before splice soldering
INNER LAYER --> OUTER LAYER |  |  |  | 42000 | MW | >1000MW
[V= 1KV 30"]
R[dc] of the Pole
I = | 1 | A
Temp.* : | 20 | °C |  | 1536 | mV
| POLE |  |  | 1536 | mW
| POLE [R20] |  |  | 1536 | mW
R[dc] of the Splice
I = | 30 | A
Temp.* : | 20 | °C |  | 1.932 | mV
| Splice |  |  | 64.4 | µW
INDUCTANCE
[Value from gain phase analyser]
|  |  |  | L | Q
[mH]
| POLE |  | 10Hz | 14.15 | 0.57
|  |  | 100Hz | 13.93 | 4.84
|  |  | 1000Hz | 13.01 | 14.43
DISCHARGE TEST
Whitout Strain
V = 100V/turn |  |  | T | 1041 | µS [Reference Pole]
| POLE | [4KV; 10 puls] | T | 1051 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends]
V = 120V/turn
| POLE |  | C.side T | 1052 | µS
|  |  | N.C. side T | 1051 | µS
[4.8KV; 10 puls]

## I003
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO |  | CONTRACT NUMBER |  | F302
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME : |  |  | INNER LAYER
CERN PART NUMBER : |  |  | HCMB__A011 |  | Serial Number : |  | I003
CERN INSPECTION & TEST PLAN NUMBER: |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | <Yes/No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | Angelo Pavese
NAME OF RESPONSIBLE |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2000-05-15 |  | TIME: |  | 0
Cable "I" Number : |  |  | 01C0002A
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 24 | °C
[5 empty] | 516 | mV
| Inner LAYER |  |  |  | 516 | mW
| Inner LAYER[R20] |  |  |  | 508.2742 | mW
INDUCTANCE | [6 empty] | ITP step 4
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Inner LAYER |  |  | 10Hz
|  |  |  | 100Hz | 1.88 | 2
|  |  |  | 1000Hz | 1.82 | 11
INSULATION RESISTANCE | [6 empty] | ITP step 6
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 19000 | MW
| Right side |  |  |  | 7900 | MW
[V = 500V 30"]
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 5
V = 120Vturn |  |  |  | T | 396 | µS [Reference layer]
| Inner LAYER [1.5KV ; 10puls] |  |  | T | 390 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120Vturn
| Inner LAYER |  |  | C.side T | 394 | µS
| [1.8KV ; 10puls] |  |  | N.C. side T | 394 | µS
LHC/MMS TRACEABILITY INFORMATION

## E003
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO |  | CONTRACT NUMBER |  | F302
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME |  |  | OUTER LAYER
CERN PART NUMBER : |  |  | HCMB__A012 |  | Serial Number : |  | E003
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | <Yes/No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | Angelo Pavese
NAME OF RESPONSIBLE |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2000-06-05 |  | TIME: |  | 0
Cable "O" Number : |  |  | 02E00213B
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 23 | °C
[5 empty] | 1026 | mV
| Outer LAYER |  |  |  | 1026 | mW
| Outer LAYER[R20] |  |  |  | 1014.4354 | mW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Outer LAYER |  |  | 10Hz
|  |  |  | 100Hz | 6.64 | 3.5
|  |  |  | 1000Hz | 6.52 | 24.4
INSULATION RESISTANCE
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 10700 | MW
| Right side |  |  |  | 14300 | MW
[V = 500V 30"]
DISCHARGE TEST
[ Whithout Strain] | [6 empty] | ITP step 5
V = 120V/turn |  |  |  | T | 744 | µS [Reference layer]
| Outer LAYER [3.0KV ; 10puls] |  |  | T | 744 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120V/turn
| Outer LAYER |  |  | C.side T | 748 | µS
|  |  |  | N.C. side T | 748 | µS
[3.0KV ; 10puls]
LHC/MMS TRACEABILITY INFORMATION

## P004
ELECTRICAL TESTS OF POLES
|  |  | [ACCEPTANCE TEST] |  | Date : | 2001-01-05
POLE TYPE : |  | MB |  |  | Serial Nr. | P004
Inner Layer Nr. |  | I002 | Cable I Nr. | 01C0004A
Outer Layer Nr. |  | E006 | Cable O Nr. | 02D00337A
INSULATION RESISTANCE
Before splice soldering
INNER LAYER --> OUTER LAYER |  |  |  | 55000 | MW | >1000MW
[V= 1KV 30"]
R[dc] of the Pole
I = | 1 | A
Temp.* : | 22.5 | °C |  | 1537 | mV
| POLE |  |  | 1537 | mW
| POLE [R20] |  |  | 1522.5359 | mW
R[dc] of the Splice
I = | 30 | A
Temp.* : | 23 | °C |  | 1.819 | mV
| Splice |  |  | 59.9144 | µW
INDUCTANCE
[Value from gain phase analyser]
|  |  |  | L | Q
[mH]
| POLE |  | 10Hz | 13.83 | 0.55
|  |  | 100Hz | 13.67 | 4.82
|  |  | 1000Hz | 12.88 | 15.83
DISCHARGE TEST
Whitout Strain
V = 100V/turn |  |  | T | 1050 | µS [Reference Pole]
| POLE | [4KV; 10 puls] | T | 1041 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends]
V = 120V/turn
| POLE |  | C.side T | 1040 | µS
|  |  | N.C. side T | 1044 | µS
[4.8KV; 10 puls]

## I002
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO |  | CONTRACT NUMBER |  | F302
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME : |  |  | INNER LAYER
CERN PART NUMBER : |  |  | HCMB__A011 |  | Serial Number : |  | I002
CERN INSPECTION & TEST PLAN NUMBER: |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | <Yes/No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | Angelo Pavese
NAME OF RESPONSIBLE |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2000-05-10 |  | TIME: |  | 0
Cable "I" Number : |  |  | 01C0004A
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 21 | °C
[5 empty] | 511 | mV
| Inner LAYER |  |  |  | 511 | mW
| Inner LAYER[R20] |  |  |  | 509.0656 | mW
INDUCTANCE | [6 empty] | ITP step 4
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Inner LAYER |  |  | 10Hz
|  |  |  | 100Hz | 1.89 | 2
|  |  |  | 1000Hz | 1.83 | 11
INSULATION RESISTANCE | [6 empty] | ITP step 6
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 11300 | MW
| Right side |  |  |  | 7100 | MW
[V = 500V 30"]
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 5
V = 120Vturn |  |  |  | T | 393 | µS [Reference layer]
| Inner LAYER [1.5KV ; 10puls] |  |  | T | 396 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120Vturn
| Inner LAYER |  |  | C.side T | 396 | µS
| [1.8KV ; 10puls] |  |  | N.C. side T | 396 | µS
LHC/MMS TRACEABILITY INFORMATION

## E006
ELECTRICAL TESTS OF LAYERS
|  |  | [ACCEPTANCE TEST] |  | Date : | 2001-01-03
LAYER TYPE: |  | OUTER |  |  | Serial Nr. | E006
Cable Reference Nr. |  | 02D00337A
|  |  | NAME OF TEST OPERATOR : |  |  | Angelo Pavese
|  |  | NAME OF RESPONSIBLE : |  |  | Bruno Caserza
R[dc] of the LAYER
I = | 1 | A
Temp.* : | 16 | °C
|  |  |  | 1021 | mV
| Outer LAYER |  |  | 1021 | mW
| Outer LAYER[R20] |  |  | 1036.7587 | mW
INDUCTANCE
[Value from gain phase analyser]
|  |  |  | L | Q
[mH]
| Outer LAYER |  | 10Hz | 6.73 | 0.41
|  |  | 100Hz | 6.69 | 3.87
|  |  | 1000Hz | 6.59 | 28.2
INSULATION RESISTANCE
[Copper wedges]
| Left side |  |  | 30000 | MW
| Right side |  |  | 35000 | MW
[V = 500V 30"]
DISCHARGE TEST
[ Whithout Strain]
V = 120V/turn |  |  | T | 740 | µS [Reference layer]
| Outer LAYER [3.0KV ; 10puls] |  | T | 740 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends]
V = 120V/turn
| Outer LAYER |  | C.side T | 748 | µS
|  |  | N.C. side T | 748 | µS
[3.0KV ; 10puls]