## CC2043
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : F462 |  |  |  | YT111 | 24.5311 | Magnet | 6.3702 | 6370.247 | 6294.7105 | 10 | 0.871 | 22.1 |  | 0.864 | 22.2
SUB CONTRACTOR : | [8 empty] | YT112 | 24.5221 | Aperture1 | 3.1855 | 3185.528 | 3147.7549 | 100 | 4.5 | 21.6 |  | 4.55 | 21.5
[9 empty] | YT121 | 24.7391 | Aperture2 | 3.1847 | 3184.715 | 3146.9516 | 1000 | 1.65 | 14.7 |  | 1.66 | 14.8
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 24.7241 | Apt1 Pup | 1.5936 | 1593.631 | 1574.7342
CERN PART NUMBER : |  |  | HCMBB_A001 |  | Serial Number : |  | 2043 |  | YT211 | 25.7702 | Apt1 Plw | 1.5919 | 1591.893 | 1573.0168 | 10 | 0.863 | 22.1 |  | 0.878 | 22.2
[9 empty] | YT212 | 25.1681 | Apt2 Pup | 1.5919 | 1591.888 | 1573.0119 | 100 | 4.55 | 21.6 |  | 4.52 | 21.5
CERN INSPECTION & TEST PLAN NUMBER : 9a To 9i |  |  |  |  | TEST NUMBER : |  | 9a to 9i |  | YT221 | 25.6537 | Apt2 Plw | 1.5928 | 1592.819 | 1573.9318 | 1000 | 1.66 | 14.6 |  | 1.67 | 14.6
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 25.6651
[15 empty] | 10 | 0.865 | 44.1 |  | 0.867 | 44.1
NAME OF TEST OPERATOR: |  |  | B.Caserza | [11 empty] | 100 | 4.55 | 43 |  | 4.54 | 43
NAME OF RESPONSIBLE: |  |  | B.Caserza | [11 empty] | 1000 | 1.65 | 29.3 |  | 1.66 | 29.4
DATE OF TEST : |  |  | 2003-08-05 |  | TIME : |  | 15:00:00 PM
[15 empty] | 10 | 0.86 | 88.2
[15 empty] | 100 | 4.54 | 86
[15 empty] | 1000 | 1.66 | 58.7
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 23 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 52 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1593.631 | 1591.893 |  | 1591.888 | 1592.819
Poles [20°C] |  | * | 1574.7342 | 1573.0168 |  | 1573.0119 | 1573.9318
D1 & D2 |  | * | 3147.7549 | mW |  | 3146.9516 | mW
Magnet |  |  | * | 6294.7105 | mW
|  | Poles Nr. | 02P00170 | 02P00172 |  | 02P00173 | 02P00171
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 24.5311 | 24.7391 |  | 25.7702 | 25.6537
|  | * | 24.5221 | 24.7241 |  | 25.1681 | 25.6651
Capacitance |  |  | ITPstep 9d/e
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 220 | nF |  | 230 | nF
D1 & D2 | --> Masse |  | 210 | nF |  | 200 | nF
Magnet | --> Masse |  | * | 400 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 22.1 | 22.1 |  | 22.2 | 22.2
|  | (Q) | 0.871 | 0.863 |  | 0.864 | 0.878
D1 & D2 |  | (L) | 44.1 | mH |  | 44.1 | mH
|  | (Q) | 0.865 |  |  | 0.867
Magnet |  |  | (L) | 88.2 | mH
|  |  | (Q) | 0.86
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 21.6 | 21.6 |  | 21.5 | 21.5
|  | (Q) | 4.5 | 4.55 |  | S16 | 4.52
D1 & D2 | * | (L) | 43 | mH |  | 43 | mH
|  | (Q) | 4.55 |  |  | 4.54
Magnet | * |  | (L) | 86 | mH
|  |  | (Q) | 4.54
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 14.7 | 14.6 |  | 14.8 | 14.6
|  | (Q) | 1.65 | 1.66 |  | 1.66 | 1.67
D1 & D2 | * | (L) | 29.3 | mH |  | 29.4 | mH
|  | (Q) | 1.65 |  |  | 1.66
Magnet | * |  | (L) | 58.7 | mH
|  |  | (Q) | 1.66
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 11.7 | GW |  | >1000MW
[V=1.0.KV, 60'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 14.4 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D1(8x) D1 |  | * | 5.8 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D2(8x) D2 |  | * | 4.58 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 19.6 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 18.1 | GW |  | >1000MW
DIELECTRIC TESTS |  |  | ITP step 9f/h
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.1 | µA |  | < 20 µA
[V=5.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.1 | µA |  | < 20 µA
[V=5.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DISCHARGE TEST |  |  | ITP step 9i
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.972 | 0.966 |  | 0.97 | 0.969
| Dipoles D1 & D2 [4KV] * |  | 1.7 | mS | * | 1.692 | mS
| Magnet [4KV] |  | * | 2.525 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=800V] |  | 215 / 209 | 207 / 205 | µS | 207 / 205 | 205 / 205 | µS
| [C= 2µF] | Current | 27.5 / 28.5 | 26.5 / 26.5 | A | 27.0 / 26.0 | 27.5 /27.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION