## Inlayer_TB
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME : |  |  | INNER LAYER
CERN PART NUMBER : |  |  | HCMB__A0011 |  | Serial Number : |  | 02I00495
CERN INSPECTION & TEST PLAN NUMBER: |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | </No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | Alessio Rocca
NAME OF RESPONSIBLE |  |  | B.Caserza
DATE OF TEST: |  |  | 2004-08-06 |  | TIME: |  | 7.45
Cable "I" Number : |  |  | 01B10534A
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 25 | °C
[5 empty] | 516 | mV
| Inner LAYER |  |  |  | 516 | mW
| Inner LAYER[R20] |  |  |  | 506.3788 | mW
INDUCTANCE | [6 empty] | ITP step 4
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Inner LAYER |  |  | 10Hz | 1.91 | 0.233
|  |  |  | 100Hz | 1.89 | 2.23
|  |  |  | 1000Hz | 1.83 | 12.13
INSULATION RESISTANCE | [6 empty] | ITP step 6
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 71000 | MW
| Right side |  |  |  | 64000 | MW
[V = 500V 30"]
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 5
V = 120Vturn |  |  |  | T | 393 | µS [Reference layer]
| Inner LAYER [1.5KV ; 10puls] |  |  | T | 366 | µS | new rack
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120Vturn
| Inner LAYER |  |  | C.side T |  | µS
| [1.8KV ; 10puls] |  |  | N.C. side T |  | µS
LHC/MMS TRACEABILITY INFORMATION