## Final_cold-A
|  |  | ELECTRICAL TESTS OF DIPOLES | [9 empty] | RAW_Data | [6 empty] | RAW_Data [Gain Phase Analyser]
COLD MASS
|  |  | (WITH END CAPS) | [5 empty] | QHs |  | Vtaps | Vtaps | Magnet |  | Spools | Spools | f | Q | L
[9 empty] | [W] |  | [V] | [mv] | R20[mW] |  | [V] | [mW] | 10 | 1.03 | 101
[8 empty] | YT111 | 24.1659 | Magnet | -6.0674 | -6067.416 | -6141.1093 | MCO(D1) | -2.2637 | -2263.718 | 100 | 4.78 | 92.7
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : F301 |  |  | YT112 | 24.1523 | EE015 | -0.0010653 | -1.0653 |  | MCD(D1) | 6.4306 | 6430.572 | 1000 | 1.46 | 52
SUB CONTRACTOR : | [7 empty] | YT121 | 24.2243 | EE013 | -0.0010653 | -1.0653 |  | MCS(D1) | -4.202 | -4201.953
[8 empty] | YT122 | 24.357 | EE111 | -0.0010695 | -1.0695 |  | MCO(D2) | -0.10489 | -104.8875
COMPONENT NAME : |  |  | COLDMASS |  |  |  |  | YT211 | 24.5803 | EE112 | -0.0010786 | -1.0786 |  | MCD(D2) | 3.1843 | 3184.285
CERN PART NUMBER : |  |  | HCMBARA001 |  | Serial Number : |  | 2039 | YT212 | 24.3458 | EE119 | -1.5178 | -1517.832 |  | MCS(D2) | -2.064 | -2063.976
[8 empty] | YT221 | 24.7084 | EE113 | -3.0344 | -3034.438 | -3070.2153
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 25a to 25p |  | TEST NUMBER : |  | 25a to 25p | YT222 | 24.6413 | EE211 | -3.0345 | -3034.459
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number | EH821[W] | 100.4651 | EE219 | -4.5517 | -4551.744
[8 empty] | TT821[W] | 68.6674 | EE212 | -6.0679 | -6067.866 | -3070.25
NAME OF TEST OPERATOR: |  |  | A.Pavese | [6 empty] | EE213 | -6.0679 | -6067.875
NAME OF RESPONSIBLE: |  |  | B.Caserza | [6 empty] | EE012 | -6.0679 | -6067.876
DATE OF TEST : |  |  | 2003-11-25 |  | TIME : |  | 10:00 |  |  | EE014 | -6.0678 | -6067.85
R[dc] of the Dipoles |  |  | ITP 25a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 17 | °C
Humidite: | 66 | %
D1 & D2 | [20°C] | * | -3070.2153 | mW | * | -3070.25 | mW
Magnet | [20°C] |  | * | -6141.1093 | mW
|  | Poles Nr. | 02P00154 | 02P00155 |  | 02P00156 | 02P00157
R[dc] of the Quench Heaters |  |  | ITP 25b/d
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
| Apt.1 & Apt. 2 |  | [W] | [W] |  | [W] | [W]
|  | * | 24.1659 | 24.2243 |  | 24.5803 | 24.7084
|  | * | 24.1523 | 24.357 |  | 24.3458 | 24.6413
| Cryogenic heater |  |  | 100.4651 | W | R[iso] >40MW | OK
67.64 | TT821 | Nr. :CX_LS_X | 16021 | 68.6674 | W | R[iso] >40MW | OK
Protection Diode |  |  |  | Forward |  | Reverse
Type: | AR | Nr.MDB | 0487 | EE014 > EE015 | ok | EE015 > EE014 | ok
R[dc] of the Spools |  |  | ITP 25c
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
| Connection Side |  | [mW] |  |  | [mW]
| MCO |  | 6430.572 | Aux11/EE841 |  | 3184.285 | Aux11/EE941
|  | Nr. MC0-MA-I- | 0151 |  |  | 0161
| MCD |  | -4201.953 | Aux11/EE851 |  | -2063.976 | Aux11/EE951
|  | Nr. MCD-MA-I- | 0151 |  |  | 0161
Lyra Side
| MCS |  | -2263.718 | Aux11/EE831 |  | -104.8875 | Aux11/EE931
|  | Nr. MCS-MA-I- | 0120 |  |  | 0192
ELECTRICAL TESTS OF DIPOLES
COLD MASS
(WITH END CAPS)
Voltage Taps |  |  | ITP 25e
|  |  |  | [mV] |  | [mV]
I = | 1 | A | EE015 | -1.0653 |  | -3034.459 | EE211
|  |  | EE013 | -1.0653 |  | -4551.744 | EE219
|  |  | EE111 | -1.0695 |  | -6067.866 | EE212
|  |  | EE112 | -1.0786 |  | -6067.875 | EE213
|  |  | EE119 | -1517.832 |  | -6067.876 | EE012
|  |  | EE113 | -3034.438 |  | -6067.85 | EE014
Capacitance |  |  | ITP 25h
[ Megger 100V ; > 1'] |  |  |  |  | MAGNET
Magnet | --> Ground |  | * | 410 | nF
INDUCTANCE L/Q[10Hz] |  |  | ITP 25g
[Value from gain phase analyser] |  |  |  |  | MAGNET
Magnet |  |  | (L) | 101 | mH
|  |  | (Q) | 1.03
INDUCTANCE L/Q[100Hz] |  |  | ITP 25g
[Value from gain phase analyser] |  |  |  |  | MAGNET
Magnet | * |  | (L) | 92.7 | mH
|  |  | (Q) | 4.78
INDUCTANCE L/Q[1.0KHz] |  |  | ITP 25g
[Value from gain phase analyser] |  |  |  |  | MAGNET
Magnet | * |  | (L) | 52 | mH
|  |  | (Q) | 1.46
ELECTRICAL TESTS OF DIPOLES
COLD MASS
(WITH END CAPS)
INSULATION RESISTANCE |  |  | ITP 25o
Magnet + QHs + Bus MB ---> Ground |  |  |  | 11.1 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs(All) Magnet |  | *
|  |  |  | 6.9 | GW |  | >1000MW
[V=1.0.KV, 60'']
Bus QF + QD ---> Ground
|  |  | * | 37.2 | GW |  | >1000MW
[V=1.0.KV, 60'']
Bus Aux.+ spools ---> Ground |  |  |  | 5.95 | GW |  | >500MW
[V=1.0KV, 60'']
Cicuits spools ----> Magnet |  |  |  | 7.65 | GW |  | >500MW
[Via Vtaps]
[V=1.0.KV, 60'']
DIELECTRIC TESTS |  |  | ITP 25i/n
Magnet + QHs + Bus MB ---> Ground |  |  |  | 0.462 | µA |  | <25µA
[V=5.0.KV, 2']
| QHs(All) Magnet |  |  | 0.294 | µA |  | <20µA
[V=3.0.KV, 2']
| Bus QF + QD ---> Ground |  |  | 0.805 | µA |  | <10µA
*
[V=5.0.KV, 2']
Bus Aux.+ spools ---> Ground |  |  |  | 0.23 | µA |  | <2.0µA
| [V=1.5KV, 1'] |  | *
DISCHARGE TEST |  |  | ITP 25m
V = | 25/Turn |  |  |  | MAGNET
[C= 2µF]
| Magnet [2KV] |  |  | 1.192 | mS
TT821 [Rdc]
|  |  | Temp.[°C] | R[4w] W |  | R[V+;I+]W | R[V-;I-] W | R(V-,I-,V+,I+)>ground
| After discharge and H.V tests |  | 17 | 68.66 |  | 3.44 | 3.48 | OVLD
Electrical Continuty of Coldmass |  |  | ITP 25p
I = | 30 | A |  |  | COLD MASS
Temp.* : | 17 | °C
| Codmass |  | * | 0.3 | mW
Magnet
LHC/MMS TRACEABILITY INFORMATION
TT821 cern
Value [W]

## Sheet3
[7 empty] | EXTERNAL VOLTAGE TAPS CONTROL |  |  |  | Date: | 2003-11-25
MBA
Temp. : | 17 | °C |  |  |  |  | [Diode Type AR]
Humidity: | 66 | %
Current: | 1 | A |  |  |  |  | Connection Side
V[mV]
Commun
(L com 50)
[8 empty] | A | EE014 | -6067.85
[9 empty] | EE012 | -6067.876
[9 empty] | EE213 | -6067.875
[9 empty] | EE212 | -6067.866
[9 empty] | EE219 | -4551.744
[9 empty] | EE211 | -3034.459
|  |  |  | Cold mass Temp. | [7 empty] | A
|  |  | TT821 | 68.6674 | W
B
[9 empty] | EE113 | -3034.438
[9 empty] | EE119 | -1517.832
[9 empty] | EE112 | -1.0786
[9 empty] | EE111 | -1.0695
[9 empty] | EE013 | -1.0653
[8 empty] | B | EE015 | -1.0653
Cryogenic heater
|  |  | EH821 | 100.4651 | W
Lyra Side
Upper Pole
inner
outer
inner
inner
inner
outer
outer
outer
Upper Pole
Lower Pole
Lower Pole
Bus Left
Bus Right
DIPOLE D2 Right
DIPOLE D1 Left
Bus Right
Bus Left

## Sheet4
[7 empty] | EXTERNAL VOLTAGE TAPS CONTROL |  |  |  | Date: | 2003-11-25
MBA
Temp. : | 17 | °C |  |  |  |  | [Diode Type AL]
Humidity: | 66 | %
Current: | 1 | A |  |  |  |  | Connection Side
V[mV]
Commun
(L com 50)
[8 empty] | A | EE014 | -6067.85
[9 empty] | EE012 | -6067.876
[9 empty] | EE213 | -6067.875
[9 empty] | EE212 | -6067.866
[9 empty] | EE219 | -4551.744
[9 empty] | EE211 | -3034.459
|  |  |  | Cold mass Temp. | [7 empty] | A
|  |  | TT821 | 68.6674 | W
B
[9 empty] | EE113 | -3034.438
[9 empty] | EE119 | -1517.832
[9 empty] | EE112 | -1.0786
[9 empty] | EE111 | -1.0695
[9 empty] | EE013 | -1.0653
[8 empty] | B | EE015 | -1.0653
Cryogenic heater
|  |  | EH821 | 100.4651 | W
Lyra Side
Upper Pole
inner
outer
inner
inner
inner
outer
outer
outer
Upper Pole
Lower Pole
Lower Pole
Bus Left
Bus Right
DIPOLE D2 Right
DIPOLE D1 Left
Bus Right
Bus Left