## 2121
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : F462 |  |  |  | YT111 | 21.2579 | Magnet | 6.0533 | 6053.33 | 5981.5514 | 10 | 0.894 | 22 |  | 0.894 | 22
SUB CONTRACTOR : | [8 empty] | YT112 | 20.9725 | Aperture1 | 3.0298 | 3029.761 | 2993.835 | 100 | 4.79 | 21.4 |  | 4.79 | 21.4
[9 empty] | YT121 | 21.7119 | Aperture2 | 3.0236 | 3023.558 | 2987.7055 | 1000 | 1.89 | 16.2 |  | 1.9 | 16.2
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.5253 | Apt1 Pup | 1.5039 | 1503.949 | 1486.1156
CERN PART NUMBER : |  |  | HCMBB_A001 |  | Serial Number : |  | 2121 |  | YT211 | 23.2286 | Apt1 Plw | 1.5258 | 1525.756 | 1507.664 | 10 | 0.894 | 22 |  | 0.896 | 22
[9 empty] | YT212 | 22.0786 | Apt2 Pup | 1.5065 | 1506.501 | 1488.6374 | 100 | 4.77 | 21.4 |  | 4.77 | 21.4
CERN INSPECTION & TEST PLAN NUMBER : 9a To 9i |  |  |  |  | TEST NUMBER : |  | 9a to 9i |  | YT221 | 21.3938 | Apt2 Plw | 1.5171 | 1517.054 | 1499.0652 | 1000 | 1.91 | 16 |  | 1.91 | 15.9
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.0819
[15 empty] | 10 | 0.894 | 44 |  | 0.894 | 44
NAME OF TEST OPERATOR: |  |  | M.Levrero | [11 empty] | 100 | 4.78 | 42.9 |  | 4.78 | 42.9
NAME OF RESPONSIBLE: |  |  | B.Caserza | [11 empty] | 1000 | 1.9 | 32.2 |  | 1.9 | 32.2
DATE OF TEST : |  |  | 2004-10-11 |  | TIME : |  | 10:45
[15 empty] | 10 | 0.894 | 88
[15 empty] | 100 | 4.77 | 85.7
[15 empty] | 1000 | 1.9 | 64.4
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 23 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 64 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1503.949 | 1525.756 |  | 1506.501 | 1517.054
Poles [20°C] |  | * | 1486.1156 | 1507.664 |  | 1488.6374 | 1499.0652
D1 & D2 |  | * | 2993.835 | mW |  | 2987.7055 | mW
Magnet |  |  | * | 5981.5514 | mW
|  | Poles Nr. | 02P00482 | 02P00483 |  | 02P00484 | 02P00485
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 21.2579 | 21.7119 |  | 23.2286 | 21.3938
|  | * | 20.9725 | 21.5253 |  | 22.0786 | 21.0819
Capacitance |  |  | ITPstep 9d/e
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 200 | nF |  | 210 | nF
D1 & D2 | --> Masse |  | 200 | nF |  | 200 | nF
Magnet | --> Masse |  | * | 400 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 22 | 22 |  | 22 | 22
|  | (Q) | 0.894 | 0.894 |  | 0.894 | 0.896
D1 & D2 |  | (L) | 44 | mH |  | 44 | mH
|  | (Q) | 0.894 |  |  | 0.894
Magnet |  |  | (L) | 88 | mH
|  |  | (Q) | 0.894
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 21.4 | 21.4 |  | 21.4 | 21.4
|  | (Q) | 4.79 | 4.77 |  | S16 | 4.77
D1 & D2 | * | (L) | 42.9 | mH |  | 42.9 | mH
|  | (Q) | 4.78 |  |  | 4.78
Magnet | * |  | (L) | 85.7 | mH
|  |  | (Q) | 4.77
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 16.2 | 16 |  | 16.2 | 15.9
|  | (Q) | 1.89 | 1.91 |  | 1.9 | 1.91
D1 & D2 | * | (L) | 32.2 | mH |  | 32.2 | mH
|  | (Q) | 1.9 |  |  | 1.9
Magnet | * |  | (L) | 64.4 | mH
|  |  | (Q) | 1.9
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 13.7 | GW |  | >1000MW
[V=1.0.KV, 60'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 7.75 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D1(8x) D1 |  | * | 10.5 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D2(8x) D2 |  | * | 7.7 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 33 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 26.8 | GW |  | >1000MW
DIELECTRIC TESTS |  |  | ITP step 9f/h
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.3 | µA |  | < 20 µA
[V=5.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.4 | µA |  | < 20 µA
[V=5.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DISCHARGE TEST |  |  | ITP step 9i
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 1 | 1 |  | 1.004 | 0.996
| Dipoles D1 & D2 [4KV] * |  | 1.76 | mS | * | 1.76 | mS
| Magnet [4KV] |  | * | 2.61 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=850V] |  | 1204 / 1174 | 1209 / 1176 | µS | 1239 / 1166 | 1209 / 1174 | µS
| [C= 7mF] | Current | 39.1 / 39.2 | 38.0 / 37.8 | A | 35.9 / 37.3 | 38.8 / 39.1 | A
Insul. Resistance All QHs --> Masse |  |  |  | 6.1 | GW |  | >1000MW
[V=3.0.KV, 60'']
Insul. Resistance All QHs ---> Magnet |  |  |  | 5.2 | GW |  | >1000MW
[V=3.0.KV, 60'']
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION

## 02P00482
ELECTRICAL TESTS OF POLES
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER :
COMPONENT NAME : |  |  | POLE
CERN PART NUMBER : |  |  | HCMB__A0010 |  | Serial Number : |  | 02P00482
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 10,11,12,13,14,&14a |  | TEST NUMBER : |  | 10,11,12,13,14&14a
NON CONFORMITY : |  |  | <No> |  | NON-CONFORMITY NUMBER : |  | <Number>
NAME OF TEST OPERATOR : |  |  | A.Menegatti
NAME OF RESPONSIBLE : |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2004-08-27 |  | TIME: |  | 11.3
Cable "I" Number : |  |  | 01B10494C |  |  | Serial Number "I" | 02I00485
Cable "O" Number : |  |  | 02B50563A |  |  | Serial Number "O" | 02E00485
INSULATION RESISTANCE
Before splice soldering | [6 empty] | ITP step 10
INNER LAYER --> OUTER LAYER |  |  |  |  | 22300 | MW | >1000MW
[V= 1KV 30"]
R[dc] of the Pole
I = | 1 | A |  |  |  |  | ITP step 11
Temp.* : | 28 | °C |  |  | 1559 | mV
| POLE |  |  |  | 1559 | mW
| POLE [R20] |  |  |  | 1513.0047 | mW
R[dc] of the Splice
I = | 30 | A |  |  |  |  | ITP step 12
Temp.* : | 26 | °C |  |  | 1.89 | mV
| Splice |  |  |  | 61.5234 | µW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 14a
[5 empty] | L | Q
[mH]
| POLE |  |  | 10Hz | 14.03 | 0.563
|  |  |  | 100Hz | 13.87 | 4.84
|  |  |  | 1000Hz | 12.89 | 13.18
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 13
V = 100V/turn |  |  |  | T | 1046 | µS [Reference Pole]
| POLE | [4KV; 10 puls] |  | T | 996 | µS | New rack
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 14
V = 120V/turn
| POLE |  |  | C.side T | 1000 | µS
|  |  |  | N.C.side | 1000 | µS
[4.8KV; 10 puls]
LHC/MMS TRACEABILITY INFORMATION

## 02I00485
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME : |  |  | INNER LAYER
CERN PART NUMBER : |  |  | HCMB__A0011 |  | Serial Number : |  | 02I00485
CERN INSPECTION & TEST PLAN NUMBER: |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | </No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | A.Menegatti
NAME OF RESPONSIBLE |  |  | B.Caserza
DATE OF TEST: |  |  | 2004-07-27 |  | TIME: |  | 15
Cable "I" Number : |  |  | 01B10494C
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 25 | °C
[5 empty] | 519 | mV
| Inner LAYER |  |  |  | 519 | mW
| Inner LAYER[R20] |  |  |  | 509.3229 | mW
INDUCTANCE | [6 empty] | ITP step 4
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Inner LAYER |  |  | 10Hz | 1.9 | 0.229
|  |  |  | 100Hz | 1.89 | 2.2
|  |  |  | 1000Hz | 1.83 | 12.02
INSULATION RESISTANCE | [6 empty] | ITP step 6
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 25000 | MW
| Right side |  |  |  | 12000 | MW
[V = 500V 30"]
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 5
V = 120Vturn |  |  |  | T | 393 | µS [Reference layer]
| Inner LAYER [1.5KV ; 10puls] |  |  | T | 366 | µS | new rack
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120Vturn
| Inner LAYER |  |  | C.side T |  | µS
| [1.8KV ; 10puls] |  |  | N.C. side T |  | µS
LHC/MMS TRACEABILITY INFORMATION

## 02E00485
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME |  |  | OUTER LAYER
CERN PART NUMBER : |  |  | HCMB__A0012 |  | Serial Number : |  | 02E00485
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | <No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | A.Rocca
NAME OF RESPONSIBLE |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2004-07-27 |  | TIME: |  | 15.45
Cable "O" Number : |  |  | 02B50563A
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 25 | °C
[5 empty] | 1037 | mV
| Outer LAYER |  |  |  | 1037 | mW
| Outer LAYER[R20] |  |  |  | 1017.6644 | mW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Outer LAYER |  |  | 10Hz | 6.73 | 0.399
|  |  |  | 100Hz | 6.71 | 3.82
|  |  |  | 1000Hz | 6.59 | 22.18
INSULATION RESISTANCE
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 36000 | MW
| Right side |  |  |  | 74000 | MW
[V = 500V 30"]
DISCHARGE TEST
[ Whithout Strain] | [6 empty] | ITP step 5
V = 120V/turn |  |  |  | T | 744 | µS [Reference layer]
| Outer LAYER [3.0KV ; 10puls] |  |  | T | 699 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120V/turn
| Outer LAYER |  |  | C.side T |  | µS
|  |  |  | N.C. side T |  | µS
[3.0KV ; 10puls]
LHC/MMS TRACEABILITY INFORMATION

## 02P00483
ELECTRICAL TESTS OF POLES
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER :
COMPONENT NAME : |  |  | POLE
CERN PART NUMBER : |  |  | HCMB__A0010 |  | Serial Number : |  | 02P00483
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 10,11,12,13,14,&14a |  | TEST NUMBER : |  | 10,11,12,13,14&14a
NON CONFORMITY : |  |  | <No> |  | NON-CONFORMITY NUMBER : |  | <Number>
NAME OF TEST OPERATOR : |  |  | A.Menegatti
NAME OF RESPONSIBLE : |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2004-08-26 |  | TIME: |  | 16.3
Cable "I" Number : |  |  | 01B10494B |  |  | Serial Number "I" | 02I00486
Cable "O" Number : |  |  | 02B50563B |  |  | Serial Number "O" | 02E00486
INSULATION RESISTANCE
Before splice soldering | [6 empty] | ITP step 10
INNER LAYER --> OUTER LAYER |  |  |  |  | 19000 | MW | >1000MW
[V= 1KV 30"]
R[dc] of the Pole
I = | 1 | A |  |  |  |  | ITP step 11
Temp.* : | 27.5 | °C |  |  | 1556 | mV
| POLE |  |  |  | 1556 | mW
| POLE [R20] |  |  |  | 1512.8828 | mW
R[dc] of the Splice
I = | 30 | A |  |  |  |  | ITP step 12
Temp.* : | 26 | °C |  |  | 1.797 | mV
| Splice |  |  |  | 58.4961 | µW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 14a
[5 empty] | L | Q
[mH]
| POLE |  |  | 10Hz | 14.34 | 0.569
|  |  |  | 100Hz | 14.14 | 4.79
|  |  |  | 1000Hz | 13.08 | 12.84
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 13
V = 100V/turn |  |  |  | T | 1046 | µS [Reference Pole]
| POLE | [4KV; 10 puls] |  | T | 1008 | µS | New rack
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 14
V = 120V/turn
| POLE |  |  | C.side T | 1012 | µS
|  |  |  | N.C.side | 1008 | µS
[4.8KV; 10 puls]
LHC/MMS TRACEABILITY INFORMATION

## 02I00486
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME : |  |  | INNER LAYER
CERN PART NUMBER : |  |  | HCMB__A0011 |  | Serial Number : |  | 02I00486
CERN INSPECTION & TEST PLAN NUMBER: |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | </No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | Alessio Rocca
NAME OF RESPONSIBLE |  |  | B.Caserza
DATE OF TEST: |  |  | 2004-07-29 |  | TIME: |  | 8
Cable "I" Number : |  |  | 01B10494B
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 23.5 | °C
[5 empty] | 522 | mV
| Inner LAYER |  |  |  | 522 | mW
| Inner LAYER[R20] |  |  |  | 515.1485 | mW
INDUCTANCE | [6 empty] | ITP step 4
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Inner LAYER |  |  | 10Hz | 1.91 | 0.23
|  |  |  | 100Hz | 1.9 | 2.21
|  |  |  | 1000Hz | 1.83 | 12.18
INSULATION RESISTANCE | [6 empty] | ITP step 6
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 47000 | MW
| Right side |  |  |  | 68000 | MW
[V = 500V 30"]
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 5
V = 120Vturn |  |  |  | T | 393 | µS [Reference layer]
| Inner LAYER [1.5KV ; 10puls] |  |  | T | 364 | µS | new rack
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120Vturn
| Inner LAYER |  |  | C.side T |  | µS
| [1.8KV ; 10puls] |  |  | N.C. side T |  | µS
LHC/MMS TRACEABILITY INFORMATION

## 02E00486
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME |  |  | OUTER LAYER
CERN PART NUMBER : |  |  | HCMB__A0012 |  | Serial Number : |  | 02E00486
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | <No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | Alessio Rocca
NAME OF RESPONSIBLE |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2004-08-02 |  | TIME: |  | 8
Cable "O" Number : |  |  | 02B50563B
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 25 | °C
[5 empty] | 1025 | mV
| Outer LAYER |  |  |  | 1025 | mW
| Outer LAYER[R20] |  |  |  | 1005.8881 | mW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Outer LAYER |  |  | 10Hz | 6.71 | 0.404
|  |  |  | 100Hz | 6.67 | 3.91
|  |  |  | 1000Hz | 6.61 | 27.48
INSULATION RESISTANCE
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 47000 | MW
| Right side |  |  |  | 59000 | MW
[V = 500V 30"]
DISCHARGE TEST
[ Whithout Strain] | [6 empty] | ITP step 5
V = 120V/turn |  |  |  | T | 744 | µS [Reference layer]
| Outer LAYER [3.0KV ; 10puls] |  |  | T | 736 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120V/turn
| Outer LAYER |  |  | C.side T |  | µS
|  |  |  | N.C. side T |  | µS
[3.0KV ; 10puls]
LHC/MMS TRACEABILITY INFORMATION

## 02P00484
ELECTRICAL TESTS OF POLES
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER :
COMPONENT NAME : |  |  | POLE
CERN PART NUMBER : |  |  | HCMB__A0010 |  | Serial Number : |  | 02P00484
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 10,11,12,13,14,&14a |  | TEST NUMBER : |  | 10,11,12,13,14&14a
NON CONFORMITY : |  |  | <No> |  | NON-CONFORMITY NUMBER : |  | <Number>
NAME OF TEST OPERATOR : |  |  | A.Menegatti
NAME OF RESPONSIBLE : |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2004-08-26 |  | TIME: |  | 12
Cable "I" Number : |  |  | 01B10494A |  |  | Serial Number "I" | 02I00487
Cable "O" Number : |  |  | 02B50563C |  |  | Serial Number "O" | 02E00487
INSULATION RESISTANCE
Before splice soldering | [6 empty] | ITP step 10
INNER LAYER --> OUTER LAYER |  |  |  |  | 13500 | MW | >1000MW
[V= 1KV 30"]
R[dc] of the Pole
I = | 1 | A |  |  |  |  | ITP step 11
Temp.* : | 27.5 | °C |  |  | 1558 | mV
| POLE |  |  |  | 1558 | mW
| POLE [R20] |  |  |  | 1514.8274 | mW
R[dc] of the Splice
I = | 30 | A |  |  |  |  | ITP step 12
Temp.* : | 29 | °C |  |  | 1.98 | mV
| Splice |  |  |  | 63.7066 | µW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 14a
[5 empty] | L | Q
[mH]
| POLE |  |  | 10Hz | 14.04 | 0.563
|  |  |  | 100Hz | 13.89 | 4.84
|  |  |  | 1000Hz | 12.92 | 13.16
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 13
V = 100V/turn |  |  |  | T | 1046 | µS [Reference Pole]
| POLE | [4KV; 10 puls] |  | T | 997 | µS | New rack
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 14
V = 120V/turn
| POLE |  |  | C.side T | 1004 | µS
|  |  |  | N.C.side | 1000 | µS
[4.8KV; 10 puls]
LHC/MMS TRACEABILITY INFORMATION

## 02I00487
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME : |  |  | INNER LAYER
CERN PART NUMBER : |  |  | HCMB__A0011 |  | Serial Number : |  | 02I00487
CERN INSPECTION & TEST PLAN NUMBER: |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | </No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | A.Menegatti
NAME OF RESPONSIBLE |  |  | B.Caserza
DATE OF TEST: |  |  | 2004-07-29 |  | TIME: |  | 8.3
Cable "I" Number : |  |  | 01B10494A
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 23.5 | °C
[5 empty] | 518 | mV
| Inner LAYER |  |  |  | 518 | mW
| Inner LAYER[R20] |  |  |  | 511.201 | mW
INDUCTANCE | [6 empty] | ITP step 4
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Inner LAYER |  |  | 10Hz | 1.9 | 0.23
|  |  |  | 100Hz | 1.89 | 2.22
|  |  |  | 1000Hz | 1.83 | 12.22
INSULATION RESISTANCE | [6 empty] | ITP step 6
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 43000 | MW
| Right side |  |  |  | 41000 | MW
[V = 500V 30"]
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 5
V = 120Vturn |  |  |  | T | 393 | µS [Reference layer]
| Inner LAYER [1.5KV ; 10puls] |  |  | T | 366 | µS | new rack
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120Vturn
| Inner LAYER |  |  | C.side T |  | µS
| [1.8KV ; 10puls] |  |  | N.C. side T |  | µS
LHC/MMS TRACEABILITY INFORMATION

## 02E00487
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME |  |  | OUTER LAYER
CERN PART NUMBER : |  |  | HCMB__A0012 |  | Serial Number : |  | 02E00487
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | <No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | A.Menegatti
NAME OF RESPONSIBLE |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2004-07-30 |  | TIME: |  | 9.45
Cable "O" Number : |  |  | 02B50563C
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 25 | °C
[5 empty] | 1038 | mV
| Outer LAYER |  |  |  | 1038 | mW
| Outer LAYER[R20] |  |  |  | 1018.6457 | mW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Outer LAYER |  |  | 10Hz | 6.79 | 0.407
|  |  |  | 100Hz | 6.63 | 3.68
|  |  |  | 1000Hz | 6.42 | 21.02
INSULATION RESISTANCE
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 56000 | MW
| Right side |  |  |  | 82000 | MW
[V = 500V 30"]
DISCHARGE TEST
[ Whithout Strain] | [6 empty] | ITP step 5
V = 120V/turn |  |  |  | T | 744 | µS [Reference layer]
| Outer LAYER [3.0KV ; 10puls] |  |  | T | 724 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120V/turn
| Outer LAYER |  |  | C.side T |  | µS
|  |  |  | N.C. side T |  | µS
[3.0KV ; 10puls]
LHC/MMS TRACEABILITY INFORMATION

## 02P00485
ELECTRICAL TESTS OF POLES
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER :
COMPONENT NAME : |  |  | POLE
CERN PART NUMBER : |  |  | HCMB__A0010 |  | Serial Number : |  | 02P00485
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 10,11,12,13,14,&14a |  | TEST NUMBER : |  | 10,11,12,13,14&14a
NON CONFORMITY : |  |  | <No> |  | NON-CONFORMITY NUMBER : |  | <Number>
NAME OF TEST OPERATOR : |  |  | A.Menegatti
NAME OF RESPONSIBLE : |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2004-08-26 |  | TIME: |  | 8.3
Cable "I" Number : |  |  | 01B10228H |  |  | Serial Number "I" | 02I00488
Cable "O" Number : |  |  | 02B50563D |  |  | Serial Number "O" | 02E00488
INSULATION RESISTANCE
Before splice soldering | [6 empty] | ITP step 10
INNER LAYER --> OUTER LAYER |  |  |  |  | 33000 | MW | >1000MW
[V= 1KV 30"]
R[dc] of the Pole
I = | 1 | A |  |  |  |  | ITP step 11
Temp.* : | 27.3 | °C |  |  | 1552 | mV
| POLE |  |  |  | 1552 | mW
| POLE [R20] |  |  |  | 1510.1096 | mW
R[dc] of the Splice
I = | 30 | A |  |  |  |  | ITP step 12
Temp.* : | 26 | °C |  |  | 1.78 | mV
| Splice |  |  |  | 57.9427 | µW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 14a
[5 empty] | L | Q
[mH]
| POLE |  |  | 10Hz | 14.26 | 0.574
|  |  |  | 100Hz | 14.07 | 4.82
|  |  |  | 1000Hz | 13.01 | 12.87
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 13
V = 100V/turn |  |  |  | T | 1046 | µS [Reference Pole]
| POLE | [4KV; 10 puls] |  | T | 1000 | µS | New rack
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 14
V = 120V/turn
| POLE |  |  | C.side T | 1008 | µS
|  |  |  | N.C.side | 1005 | µS
[4.8KV; 10 puls]
LHC/MMS TRACEABILITY INFORMATION

## 02I00488
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME : |  |  | INNER LAYER
CERN PART NUMBER : |  |  | HCMB__A0011 |  | Serial Number : |  | 02I00488
CERN INSPECTION & TEST PLAN NUMBER: |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | </No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | A.Menegatti
NAME OF RESPONSIBLE |  |  | B.Caserza
DATE OF TEST: |  |  | 2004-07-29 |  | TIME: |  | 9
Cable "I" Number : |  |  | 01B10228H
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 23.5 | °C
[5 empty] | 518 | mV
| Inner LAYER |  |  |  | 518 | mW
| Inner LAYER[R20] |  |  |  | 511.201 | mW
INDUCTANCE | [6 empty] | ITP step 4
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Inner LAYER |  |  | 10Hz | 1.9 | 0.23
|  |  |  | 100Hz | 1.89 | 2.22
|  |  |  | 1000Hz | 1.83 | 12.22
INSULATION RESISTANCE | [6 empty] | ITP step 6
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 43000 | MW
| Right side |  |  |  | 41000 | MW
[V = 500V 30"]
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 5
V = 120Vturn |  |  |  | T | 393 | µS [Reference layer]
| Inner LAYER [1.5KV ; 10puls] |  |  | T | 366 | µS | new rack
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120Vturn
| Inner LAYER |  |  | C.side T |  | µS
| [1.8KV ; 10puls] |  |  | N.C. side T |  | µS
LHC/MMS TRACEABILITY INFORMATION

## 02E00488
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER
COMPONENT NAME |  |  | OUTER LAYER
CERN PART NUMBER : |  |  | HCMB__A0012 |  | Serial Number : |  | 02E00488
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | <No> |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | Alessio Rocca
NAME OF RESPONSIBLE |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2004-08-02 |  | TIME: |  | 8
Cable "O" Number : |  |  | 02B50563D
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 25 | °C
[5 empty] | 1033 | mV
| Outer LAYER |  |  |  | 1033 | mW
| Outer LAYER[R20] |  |  |  | 1013.739 | mW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Outer LAYER |  |  | 10Hz | 6.67 | 0.398
|  |  |  | 100Hz | 6.55 | 3.75
|  |  |  | 1000Hz | 6.43 | 25.25
INSULATION RESISTANCE
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | 65000 | MW
| Right side |  |  |  | 39000 | MW
[V = 500V 30"]
DISCHARGE TEST
[ Whithout Strain] | [6 empty] | ITP step 5
V = 120V/turn |  |  |  | T | 744 | µS [Reference layer]
| Outer LAYER [3.0KV ; 10puls] |  |  | T | 728 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120V/turn
| Outer LAYER |  |  | C.side T |  | µS
|  |  |  | N.C. side T |  | µS
[3.0KV ; 10puls]
LHC/MMS TRACEABILITY INFORMATION