## Coldmass.B
|  |  | ELECTRICAL TESTS OF DIPOLES | [9 empty] | RAW_Data | [9 empty] | RAW_Data [Gain Phase Analyser]
COLD MASS
|  |  | (WITHOUT END CAPS) | [5 empty] | QHs |  | Poles | Poles | Poles |  | Vtaps | Vtaps |  | Spools | Spools
[9 empty] | [W] |  | [V] | [mW] | R20[mW] |  | [V] | [mV] |  | [V] | [mW] | f | Q | L |  | Q | L
[8 empty] | YT111 | 20.9138 | Magnet | 6.0974 | 6097.382 | 6121.8695 | EE015 | 0.00082215 | 0.82215 | MCS(D1) | 0.20107 | 201.0684 | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : F302 |  |  | YT112 | 20.5811 | Aperture1 | 3.0471 | 3047.1 | 3059.3373 | EE013 | 0.00084144 | 0.84144 | MCS(D2) | 0.19839 | 198.3898 | 10 | 1.02 | 24.9 |  | 1.01 | 24.8
SUB CONTRACTOR : | [7 empty] | YT121 | 21.5186 | Aperture2 | 3.0503 | 3050.278 | 3062.5281 | EE111 | 0.00085247 | 0.85247 |  |  |  | 100 | 3.98 | 23.7 |  | 3.98 | 23.7
[8 empty] | YT122 | 21.0446 | Apt1 Pup | 1.5196 | 1519.635 | 1525.738 | EE112 | 0.00086574 | 0.86574 |  |  |  | 1000 | 1.21 | 13.7 |  | 1.22 | 13.6
COMPONENT NAME : |  |  | COLDMASS |  |  |  |  | YT211 | 21.32 | Apt1 Plw | 1.5275 | 1527.459 | 1533.5934 | EE119 | 1.52 | 1520.002
CERN PART NUMBER : |  |  | HCMBB_A001 |  | Serial Number : |  | 000004 | YT212 | 20.9347 | Apt2 Pup | 1.5243 | 1524.331 | 1530.4528 | EE113 | 3.032 | 3031.982 |  |  |  | 10 | 1.01 | 24.9 |  | 1.01 | 24.9
[8 empty] | YT221 | 20.5683 | Apt2 Plw | 1.5259 | 1525.946 | 1532.0743 | EE211 | 3.032 | 3031.994 |  |  |  | 100 | 4.01 | 23.7 |  | 4.01 | 23.8
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 18a to 18u |  | TEST NUMBER : |  | 18a to 18u | YT222 | 20.5222 | EH821[W] | 101.434 |  |  | EE219 | 4.5487 | 4548.672 |  |  |  | 1000 | 1.32 | 13.8 |  | 1.35 | 13.7
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  |  | TT821[W] | 64.996 |  |  | EE212 | 6.0642 | 6064.23
[14 empty] | EE213 | 6.0642 | 6064.233 |  |  |  | 10 | 1.01 | 49.7 |  | 1.01 | 49.7
NAME OF TEST OPERATOR: |  |  | A.Pavese | [10 empty] | EE012 | 6.0642 | 6064.232 |  |  |  | 100 | 3.98 | 47.4 |  | 4.02 | 47.5
NAME OF RESPONSIBLE: |  |  | B.Caserza | [10 empty] | EE014 | 6.0642 | 6064.24 |  |  |  | 1000 | 1.22 | 27.5 |  | 1.34 | 27.5
DATE OF TEST : |  |  | 2002-10-16 |  | TIME : | 9:50
[20 empty] | 10 | 1.02 | 99.5
[20 empty] | 100 | 4.06 | 95
R[dc] of the Poles |  |  | ITP 18a | [16 empty] | 1000 | 1.29 | 55.3
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 78 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1519.635 | 1527.459 |  | 1524.331 | 1525.946
Poles | [20°C] | * | 1525.738 | 1533.5934 |  | 1530.4528 | 1532.0743
D1 & D2 | [20°C] | * | 3059.3373 | mW |  | 3062.5281 | mW
Magnet | [20°C] |  | * | 6121.8695 | mW
|  | Poles Nr. | P019 | P020 |  | P014 | P021
R[dc] of the Quench Heaters |  |  | ITP 18b/d
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
| Apt.1 & Apt. 2 |  | [W] | [W] |  | [W] | [W]
|  | * | 20.9138 | 21.5186 |  | 21.32 | 20.5683
|  | * | 20.5811 | 21.0446 |  | 20.9347 | 20.5222
| Cryogenic heater |  |  | 101.434 | W | R[iso] >40MW | OK
64.67 | TT821 | Nr. :CX_LS_X | O9320 | 64.996 | W | R[iso] >40MW | OK
R[dc] of Jonction
I = | 10 | A
Temp. | 22 | °C
|  | Bus IN (Apt1) | Apt 1 | Apt 2 |  | Inter Dipoles | Bus OUT (Apt2)
|  | EE111/112 |  |  |  | EE113/211 | EE212/213
R[20°C] | [mW] | 12.996 | 16.3 | 19.6 |  | 19.2 | 12.9
| [mV] | 0.131 | 0.163 | 0.196 |  | 0.192 | 0.129
R[dc] of the Spools |  |  | ITP 18c
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
| Lyra Side |  | [mW] |  |  | [mW]
| MCS |  | 201.0684 | EE831/Aux.10 |  | 198.3898 | EE931/Aux.20
|  | MCS Nr. | MCS-MA-E0108 |  |  | MCS-MA-E0105
ELECTRICAL TESTS OF DIPOLES
COLD MASS
(WITHOUT END CAPS)
Voltage Taps |  |  | ITP 18o
|  |  |  | [mV] |  | [mV]
I = | 1 | A
|  |  | EE015 | 0.82215 |  | 3031.994 | EE211
|  |  | EE013 | 0.84144 |  | 4548.672 | EE219
|  |  | EE111 | 0.85247 |  | 6064.23 | EE212
|  |  | EE112 | 0.86574 |  | 6064.233 | EE213
|  |  | EE119 | 1520.002 |  | 6064.232 | EE012
|  |  | EE113 | 3031.982 |  | 6064.24 | EE014
Capacitance |  |  | ITP 18g/h
[ Megger 1000V ; > 1'] |  |  |  |  | MAGNET
QHs (All) | --> Magnet |  |  | 430 | nF
Magnet | --> Ground |  | * | 430 | nF
INDUCTANCE L/Q[10Hz] |  |  | ITP 18f
[Value from gain phase analyser] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 24.9 | 24.9 |  | 24.8 | 24.9
|  | (Q) | 1.02 | 1.01 |  | 1.01 | 1.01
D1 & D2 |  | (L) | 49.7 | mH |  | 49.7 | mH
|  | (Q) | 1.01 |  |  | 1.01
Magnet |  |  | (L) | 99.5 | mH
|  |  | (Q) | 1.02
INDUCTANCE L/Q[100Hz] |  |  | ITP 18f
[Value from gain phase analyser] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 23.7 | 23.7 |  | 23.7 | 23.8
|  | (Q) | 3.98 | 4.01 |  | 3.98 | 4.01
D1 & D2 | * | (L) | 47.4 | mH |  | 47.5 | mH
|  | (Q) | 3.98 |  |  | 4.02
Magnet | * |  | (L) | 95 | mH
|  |  | (Q) | 4.06
INDUCTANCE L/Q[1.0KHz] |  |  | ITP 18f
[Value from gain phase analyser] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 13.7 | 13.8 |  | 13.6 | 13.7
|  | (Q) | 1.21 | 1.32 |  | 1.22 | 1.35
D1 & D2 | * | (L) | 27.5 |  |  | 27.5 | mH
|  | (Q) | 1.22 |  |  | 1.34
Magnet | * |  | (L) | 55.3 | mH
|  |  | (Q) | 1.29
ELECTRICAL TESTS OF DIPOLES
COLD MASS
(WITHOUT END CAPS)
INSULATION RESISTANCE |  |  | ITP 18s to u
Magnet + QHs + Bus MB ---> Ground |  |  |  | 1.2 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs(All) Magnet |  | *
|  |  |  | 1.2 | GW |  | >1000MW
[V=1.0.KV, 60'']
| Bus MB Left ---> Bus MB Right |  | * | 6.75 | GW |  | >1000MW
[V=1.0.KV, 60'']
| Bus QF + QD ---> Ground |  | * | 0.93 | GW |  | >1000MW
[V=1.0.KV, 60'']
Bus QF Left ---> QF Right
| Bus QD Left ---> QD Right |  | * | 1.53 | GW |  | >1000MW
[V=1.0KV, 30'']
Bus Aux.+ spools [slot QF] ---> Bus QF |  |  |  | 6.5 | GW |  | >1000MW
Bus Aux.+ spools [slot QD] ---> Bus QD |  |  |  | 10.4 | GW |  | >1000MW
[V=1.0KV, 30'']
Bus Aux.+ spools ---> Ground |  |  |  | 2.82 | GW |  | >1000MW
[V=1.0KV, 30'']
Bus Aux. > Bus Aux. |  | (pair to Impair) |  | 2.4 | GW |  | >1000MW
[1.5KV, 1']
DIELECTRIC TESTS |  |  | ITP 18i-p to r
Magnet + QHs + Bus MB ---> Ground |  |  |  | 8.8 | µA |  | <25.0µA
[V=5.0.KV, 5']
| QHs(All) Magnet |  |  | 4.3 | µA |  | <20.0µA
[V=3.0.KV, 5']
| Bus MB Left --->Bus MB Right |  |  | 1.73 | µA |  | <10.0µA
[V=5.0.KV, 5']
| Bus QF + QD ---> Ground |  |  | 8.55 | µA |  | <10.0µA
*
[V=5.0.KV, 5']
Bus QF Left ---> QF Right
| Bus QD Left ---> QD Right |  | * | 6.45 | µA |  | <10.0µA
[V=5.0KV, 5']
Bus Aux.+ spools ---> Ground |  |  |  | 0.58 | µA |  | <2.0µA
| [V=1.50KV, 1'] |  | *
DISCHARGE TEST |  |  | ITP 18m/n
V = 70V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [2.8KV] | * | 0.9902 | 0.968 |  | 0..988 | 0.959
| Dipoles D1 & D2 [4KV] * |  | 1.748 | mS | * | 1.748 | mS
| Magnet [4KV] |  | * | 2.68 | mS
TT821 [Rdc]
|  |  | Temp.[°C] | R[4w] W |  | R[V+;I+]W | R[V-;I-] W
| After discharge and H.V tests |  | 20.6 | 64.88 |  | 8.45 | 8.48
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION
TT821 cern
Value [W]

## Vtaps
[6 empty] | EXTERNAL VOLTAGE TAPS CONTROL |  |  | Date: | 2002-10-16
MBB
Temp. : | 19 | °C
Humidity: | 78 | %
Current: | 1 | A
|  |  | V[mV] |  |  |  | Connection Side
Commun
(L com 50)
|  |  | 0.82215 | EE015 | B
|  |  | 0.84144 | EE013
|  |  | 0.85247 | EE111
|  |  | 0.86574 | EE112
|  |  | 1520.002 | EE119
|  |  | 3031.982 | EE113
|  | B | [7 empty] | Cold mass Temp.
[9 empty] | TT821 | 64.996 | W
TT821
A
|  |  | 3031.994 | EE211
|  |  | 4548.672 | EE219
|  |  | 6064.23 | EE212
|  |  | 6064.233 | EE213
|  |  | 6064.232 | EE012
|  |  | 6064.24 | EE014 | A |  |  |  |  | Cryogenic heater
[9 empty] | EH821 | 101.434 | W
Lyra Side
Upper Pole
inner
outer
inner
inner
inner
outer
outer
outer
Upper Pole
Lower Pole
Lower Pole
Bus Right
Bus Left
DIPOLE D1 Left
DIPOLE D2 Right
Bus Left
Bus Right