## Sheet1
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : F302 |  |  |  | YT111 | 20.837 | Magnet | 6.0774 | 6077.362 | 6029.129 | 10 | 0.881 | 21.7 |  | 0.88 | 21.6
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  |  |  | YT112 | 20.5016 | Aperture1 | 3.0365 | 3036.513 | 3012.4137 | 100 | 5.67 | 21.2 |  | 5.64 | 21.3
[9 empty] | YT121 | 21.3415 | Aperture2 | 3.0408 | 3040.813 | 3016.6796 | 1000 | 2.37 | 18.8 |  | 2.35 | 18.9
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.2202 | Apt1 Pup | 1.5176 | 1517.606 | 1505.5615
CERN PART NUMBER : |  |  | HCMB_A001 |  | Serial Number : |  | M007 |  | YT211 | 21.1193 | Apt1 Plw | 1.5189 | 1518.869 | 1506.8145 | 10 | 0.88 | 21.6 |  | 0.881 | 21.6
[9 empty] | YT212 | 20.8137 | Apt2 Pup | 1.5177 | 1517.715 | 1505.6696 | 100 | 5.61 | 21.3 |  | 5.61 | 21.3
CERN INSPECTION & TEST PLAN NUMBER : 16 To 18 |  |  |  |  | TEST NUMBER : |  | 16 to 18 |  | YT221 | 21.2523 | Apt2 Plw | 1.523 | 1523.043 | 1510.9554 | 1000 | 2.4 | 18.5 |  | 2.32 | 18.5
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.8548
[15 empty] | 10 | 0.881 | 21.6 |  | 0.88 | 43.3
NAME OF TEST OPERATOR: |  |  | A.Pavese | [11 empty] | 100 | 5.61 | 21.3 |  | 5.6 | 42.8
NAME OF RESPONSIBLE: |  |  | B.Caserza | [11 empty] | 1000 | 2.32 | 18.5 |  | 2.37 | 38
DATE OF TEST : |  |  | 2002-01-29 |  | TIME : |  | 0:00
[15 empty] | 10 | 0.881 | 43.3
[15 empty] | 100 | 5.65 | 42.7
[15 empty] | 1000 | 2.37 | 37.7
R[dc] of the Poles
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 22 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 44 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1517.606 | 1518.869 |  | 1517.715 | 1523.043
Poles [20°C] |  | * | 1505.5615 | 1506.8145 |  | 1505.6696 | 1510.9554
D1 & D2 |  | * | 3012.4137 | mW |  | 3016.6796 | mW
Magnet |  |  | * | 6029.129 | mW
|  | Poles Nr. | P023 | P025 |  | P022 | P024
R[dc] of the Quench Heaters
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 20.837 | 21.3415 |  | 21.1193 | 21.2523
|  | * | 20.5016 | 21.2202 |  | 20.8137 | 20.8548
Capacitance
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 270 | nF |  | 290 | nF
D1 & D2 | --> Masse |  | 380 | nF |  | 380 | nF
Magnet | --> Masse |  | * | 420 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.7 | 21.6 |  | 21.6 | 21.6
|  | (Q) | 0.881 | 0.88 |  | 0.88 | 0.881
D1 & D2 |  | (L) | 21.6 | mH |  | 43.3 | mH
|  | (Q) | 0.881 |  |  | 0.88
Magnet |  |  | (L) | 43.3 | mH
|  |  | (Q) | 0.881
INDUCTANCE L/Q[100Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 21.2 | 21.3 |  | 21.3 | 21.3
|  | (Q) | 5.67 | 5.61 |  | S16 | 5.61
D1 & D2 | * | (L) | 21.3 | mH |  | 42.8 | mH
|  | (Q) | 5.61 |  |  | 5.6
Magnet | * |  | (L) | 42.7 | mH
|  |  | (Q) | 5.65
INDUCTANCE L/Q[1.0KHz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 18.8 | 18.5 |  | 18.9 | 18.5
|  | (Q) | 2.37 | 2.4 |  | 2.35 | 2.32
D1 & D2 | * | (L) | 18.5 | mH |  | 38 | mH
|  | (Q) | 2.32 |  |  | 2.37
Magnet | * |  | (L) | 37.7 | mH
|  |  | (Q) | 2.37
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 4.06 | GW |  | >1000MW
[V=1.0.KV, 60'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 5.05 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D1(8x) D1 |  | * | 3.24 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D2(8x) D2 |  | * | 3.123 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 10.9 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 11.6 | GW |  | >1000MW
[V=1.0KV, 60'']
DIELECTRIC TESTS
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.4 | µA |  | < 20 µA
[V=5.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.2 | µA |  | < 20 µA
[V=5.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V=3.0 KV 5']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V= 3.0 KV 5']
DISCHARGE TEST
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.996 | 0.996 |  | 0.996 | 1
| Dipoles D1 & D2 [4KV] * |  | 1.789 | mS | * | 1.789 | mS
| Magnet [4KV] |  | * | 2.666 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=800V] | t | 184 / 177 | 176 / 178 | µS | 177 /177 | 177 / 177 | µS
| [C= 2µF] | Current | 32.0 / 30.0 | 29.5 /30.0 | A | 30.0 /30.0 | 30.0 / 30.0 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION