## Final_cold-B
|  |  | ELECTRICAL TESTS OF DIPOLES | [9 empty] | RAW_Data | [6 empty] | RAW_Data [Gain Phase Analyser]
COLD MASS
|  |  | (WITH END CAPS) | [5 empty] | QHs |  | Vtaps | Vtaps | Magnet |  | Spools | Spools | f | Q | L
[9 empty] | [W] |  | [V] | [mv] | R20[mW] |  | [V] | [mW] | 10 | 1.03 | 105
[8 empty] | YT111 | 21.8995 | Magnet | -6.1598 | -6159.762 | -6036.5668 | MCS(D1) | 1.3852 | 1385.151 | 100 | 84.3 | 102
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : F302 |  |  | YT112 | 20.9257 | EE015 | -0.22561 | -225.6061 |  | MCS(D2) | 0.5175 | 517.4988 | 1000 | 15.4 | 62.3
SUB CONTRACTOR : | [7 empty] | YT121 | 20.8937 | EE013 | -0.22561 | -225.6059
[8 empty] | YT122 | 20.7428 | EE111 | -0.22561 | -225.6122
COMPONENT NAME : |  |  | COLDMASS |  |  |  |  | YT211 | 20.8793 | EE112 | -0.22562 | -225.6203
CERN PART NUMBER : |  |  | HCMBB_A001 |  | Serial Number : |  | 2008 | YT212 | 21.464 | EE119 | -1.7333 | -1733.27
[8 empty] | YT221 | 20.6824 | EE113 | -3.2408 | -3240.816 | -2954.9059
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 25a to 25p |  | TEST NUMBER : |  | 25a to 25p | YT222 | 20.8389 | EE211 | -3.2408 | -3240.832
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number | EH821[W] | 100.9721 | EE219 | -4.7491 | -4749.119
[8 empty] | TT821[W] | 85.293 | EE212 | -6.2556 | -6255.581 | -2954.454
NAME OF TEST OPERATOR: |  |  | A.Pavese | [6 empty] | EE213 | -6.2556 | -6255.591
NAME OF RESPONSIBLE: |  |  | B.Caserza | [6 empty] | EE012 | -6.2556 | -6255.582
DATE OF TEST : |  |  | 2003-03-21 |  | TIME : |  | 15:30 |  |  | EE014 | -6.2556 | -6255.574
R[dc] of the Dipoles |  |  | ITP 25a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 15 | °C
Humidite: | 38 | %
D1 & D2 | [20°C] | * | -2954.9059 | mW | * | -2954.454 | mW
Magnet | [20°C] |  | * | -6036.5668 | mW
|  | Poles Nr. | 02P00026 | 02P00029 |  | 02P00028 | 02P00027
R[dc] of the Quench Heaters |  |  | ITP 25b/d
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
| Apt.1 & Apt. 2 |  | [W] | [W] |  | [W] | [W]
|  | * | 21.8995 | 20.8937 |  | 20.8793 | 20.6824
|  | * | 20.9257 | 20.7428 |  | 21.464 | 20.8389
| Cryogenic heater |  |  | 100.9721 | W | R[iso] >40MW | OK
84.49 | TT821 | Nr. :CX_LS_X | O9322 | 85.293 | W | R[iso] >40MW | OK
R[dc] of the Spools |  |  | ITP 25c
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
| Lyra Side |  | [mW] |  |  | [mW]
| Circuit MCS (Apt.1 + Apt.2) |  | 517.4988 | Bus 11/EE831 |  | 1385.151 | Bus 11/EE931
|  | MCS Nr. | MCS-MA-E0261 |  |  | MCS-MA-E0262
ELECTRICAL TESTS OF DIPOLES
COLD MASS
(WITH END CAPS)
Voltage Taps |  |  | ITP 25e
|  |  |  | [mV] |  | [mV]
I = | 1 | A | EE015 | -225.6061 |  | -3240.832 | EE211
|  |  | EE013 | -225.6059 |  | -4749.119 | EE219
|  |  | EE111 | -225.6122 |  | -6255.581 | EE212
|  |  | EE112 | -225.6203 |  | -6255.591 | EE213
|  |  | EE119 | -1733.27 |  | -6255.582 | EE012
|  |  | EE113 | -3240.816 |  | -6255.574 | EE014
Capacitance |  |  | ITP 25h
[ Megger 100V ; > 1'] |  |  |  |  | MAGNET
Magnet | --> Ground |  | * | 430 | nF
INDUCTANCE L/Q[10Hz] |  |  | ITP 25g
[Value from gain phase analyser] |  |  |  |  | MAGNET
Magnet |  |  | (L) | 105 | mH
|  |  | (Q) | 1.03
INDUCTANCE L/Q[100Hz] |  |  | ITP 25g
[Value from gain phase analyser] |  |  |  |  | MAGNET
Magnet | * |  | (L) | 102 | mH
|  |  | (Q) | 84.3
INDUCTANCE L/Q[1.0KHz] |  |  | ITP 25g
[Value from gain phase analyser] |  |  |  |  | MAGNET
Magnet | * |  | (L) | 62.3 | mH
|  |  | (Q) | 15.4
ELECTRICAL TESTS OF DIPOLES
COLD MASS
(WITH END CAPS)
INSULATION RESISTANCE |  |  | ITP 25o
Magnet + QHs + Bus MB ---> Ground |  |  |  | 5.9 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs(All) Magnet |  | *
|  |  |  | 2.28 | GW |  | >1000MW
[V=1.0.KV, 60'']
Bus QF + QD ---> Ground
|  |  |  | 90 | GW |  | >1000MW
[V=1.0.KV, 60'']
Circuit spools [Bus 18/19] ---> Ground |  |  |  | 63 | GW |  | >1000MW
Bus [11/12] --> Ground |  |  |  | 290 | GW |  | >1000MW
[V=1.5KV, 60'']
DIELECTRIC TESTS |  |  | ITP 25i/n
Magnet + QHs + Bus MB ---> Ground |  |  |  | 0.1 | µA |  | <25µA
[V=5.0.KV, 2']
| QHs(All) Magnet |  |  | 1.8 | µA |  | <20µA
[V=3.0.KV, 2']
| Bus QF + QD ---> Ground |  |  | 0.1 | µA |  | <10µA
*
[V=5.0.KV, 2']
Bus Aux.+ spools ---> Ground |  |  |  | 0.0262 | µA |  | <2.0µA
[V=1.5KV, 1']
DISCHARGE TEST |  |  | ITP 25m
V = | 25V/turn |  |  |  | MAGNET
[C= 2µF]
| Magnet [2KV] |  |  | 1.303 | mS
Electrical Continuty of Coldmass |  |  | ITP 25p
I = | 20 | A |  |  | COLD MASS
Temp.* : | 15 | °C
| Coldmass |  | * | 0.31 | mW
TT821 [Rdc]
|  |  | Temp.[°C] | R[4w] W |  | R[V+;I+]W | R[V-;I-] W
| After discharge and H.V tests |  | 15 | 85.3 |  | 7.47 | 7.48
Magnet
LHC/MMS TRACEABILITY INFORMATION
TT821 cern
Value [W]

## Sheet3
[6 empty] | EXTERNAL VOLTAGE TAPS CONTROL |  |  |  | Date: | 2003-03-21
MBB
Temp. : | 20 | °C |  |  |  | [Diode Type AR]
Humidity: | 50 | %
Current: | 1 | A
|  |  | V[mV] |  |  |  | Connection Side
Commun
(L com 50)
|  |  | -225.6061 | EE015 | B
|  |  | -225.6059 | EE013
|  |  | -225.6122 | EE111
|  |  | -225.6203 | EE112
|  |  | -1733.27 | EE119
|  |  | -3240.816 | EE113
|  | B | [7 empty] | Cold mass Temp.
[9 empty] | TT821 | 85.293 | W
TT821
A
|  |  | -3240.832 | EE211
|  |  | -4749.119 | EE219
|  |  | -6255.581 | EE212
|  |  | -6255.591 | EE213
|  |  | -6255.582 | EE012
|  |  | -6255.574 | EE014 | A |  |  |  |  | Cryogenic heater
[9 empty] | EH821 | 100.9721 | W
Lyra Side
Upper Pole
inner
outer
inner
inner
inner
outer
outer
outer
Upper Pole
Lower Pole
Lower Pole
Bus Right
Bus Left
DIPOLE D1 Left
DIPOLE D2 Right
Bus Left
Bus Right

## Sheet4
[6 empty] | EXTERNAL VOLTAGE TAPS CONTROL |  |  |  | Date: | 2003-03-21
MBB
Temp. : | 20 | °C |  |  |  | [Diode Type AL]
Humidity: | 50 | %
Current: | 1 | A |  |  |  |  | Connection Side
V[mV]
Commun
(L com 50)
|  |  | -225.6061 | EE015 | B
|  |  | -225.6059 | EE013
|  |  | -225.6122 | EE111
|  |  | -225.6203 | EE112
|  |  | -1733.27 | EE119
|  |  | -3240.816 | EE113
|  | A | [8 empty] | Cold mass Temp.
[10 empty] | TT821 | 85.293 | W
TT821
B
|  |  | -3240.832 | EE211
|  |  | -4749.119 | EE219
|  |  | -6255.581 | EE212
|  |  | -6255.591 | EE213
|  |  | -6255.582 | EE012
|  |  | -6255.574 | EE014 | A | [5 empty] | Cryogenic heater
[10 empty] | EH821 | 100.9721 | W
Lyra Side
Upper Pole
inner
outer
inner
inner
inner
outer
outer
outer
Upper Pole
Lower Pole
Lower Pole
Bus Right
Bus Left
DIPOLE D1 Left
DIPOLE D2 Right
Bus Left
Bus Right