## Sheet1
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : F302 |  |  |  | YT111 | 20.7494 | Magnet | 6.1203 | 6120.305 | 6095.9213 | 10 | 0.883 | 21.7 |  | 0.883 | 21.7
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  |  |  | YT112 | 21.1354 | Aperture1 | 3.0589 | 3058.91 | 3046.7231 | 100 | 4.64 | 21.3 |  | 4.63 | 21.2
[9 empty] | YT121 | 20.5918 | Aperture2 | 3.0614 | 3061.393 | 3049.1962 | 1000 | 1.63 | 14.8 |  | 1.63 | 14.8
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.2959 | Apt1 Pup | 1.53 | 1530.008 | 1523.9124
CERN PART NUMBER : |  |  | HCMB_A001 |  | Serial Number : |  | M010 |  | YT211 | 20.6664 | Apt1 Plw | 1.5289 | 1528.89 | 1522.7988 | 10 | 0.883 | 21.7 |  | 0.882 | 21.7
[9 empty] | YT212 | 21.0601 | Apt2 Pup | 1.5308 | 1530.795 | 1524.6962 | 100 | 4.64 | 21.2 |  | 4.63 | 21.2
CERN INSPECTION & TEST PLAN NUMBER : 16 To 18 |  |  |  |  | TEST NUMBER : |  | 16 to 18 |  | YT221 | 21.0165 | Apt2 Plw | 1.5306 | 1530.59 | 1524.492 | 1000 | 1.65 | 14.6 |  | 1.65 | 14.6
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.277
[15 empty] | 10 | 0.883 | 43.4 |  | 0.883 | 43.4
NAME OF TEST OPERATOR: |  |  | A.Pavese | [11 empty] | 100 | 4.64 | 42.5 |  | 4.63 | 42.5
NAME OF RESPONSIBLE: |  |  | B.Caserza | [11 empty] | 1000 | 1.64 | 29.4 |  | 1.64 | 29.3
DATE OF TEST : |  |  | 2002-05-15 |  | TIME : |  | 0:00
[15 empty] | 10 | 0.888 | 87.3
[15 empty] | 100 | 4.7 | 85
[15 empty] | 1000 | 1.65 | 58.9
R[dc] of the Poles
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 21 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 60 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1530.008 | 1528.89 |  | 1530.795 | 1530.59
Poles [20°C] |  | * | 1523.9124 | 1522.7988 |  | 1524.6962 | 1524.492
D1 & D2 |  | * | 3046.7231 | mW |  | 3049.1962 | mW
Magnet |  |  | * | 6095.9213 | mW
|  | Poles Nr. | P038 | P039 |  | P040 | P041
R[dc] of the Quench Heaters
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 20.7494 | 20.5918 |  | 20.6664 | 21.0165
|  | * | 21.1354 | 21.2959 |  | 21.0601 | 21.277
Capacitance
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 270 | nF |  | 250 | nF
D1 & D2 | --> Masse |  | 390 | nF |  | 390 | nF
Magnet | --> Masse |  | * | 430 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.7 | 21.7 |  | 21.7 | 21.7
|  | (Q) | 0.883 | 0.883 |  | 0.883 | 0.882
D1 & D2 |  | (L) | 43.4 | mH |  | 43.4 | mH
|  | (Q) | 0.883 |  |  | 0.883
Magnet |  |  | (L) | 87.3 | mH
|  |  | (Q) | 0.888
INDUCTANCE L/Q[100Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 21.3 | 21.2 |  | 21.2 | 21.2
|  | (Q) | 4.64 | 4.64 |  | S16 | 4.63
D1 & D2 | * | (L) | 42.5 | mH |  | 42.5 | mH
|  | (Q) | 4.64 |  |  | 4.63
Magnet | * |  | (L) | 85 | mH
|  |  | (Q) | 4.7
INDUCTANCE L/Q[1.0KHz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 14.8 | 14.6 |  | 14.8 | 14.6
|  | (Q) | 1.63 | 1.65 |  | 1.63 | 1.65
D1 & D2 | * | (L) | 29.4 | mH |  | 29.3 | mH
|  | (Q) | 1.64 |  |  | 1.64
Magnet | * |  | (L) | 58.9 | mH
|  |  | (Q) | 1.65
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 1.58 | GW |  | >1000MW
[V=1.0.KV, 60'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 1.7 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D1(8x) D1 |  | * | 1.75 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D2(8x) D2 |  | * | 2.08 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 5.9 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 6.25 | GW |  | >1000MW
[V=1.0KV, 60'']
DIELECTRIC TESTS
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 8.3 | µA |  | < 20 µA
[V=5.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 4.5 | µA |  | < 20 µA
[V=5.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V=3.0 KV 5']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V= 3.0 KV 5']
DISCHARGE TEST
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.98 | 0.968 |  | 0.98 | 0.948
| Dipoles D1 & D2 [4KV] * |  | 1.709 | mS | * | 1.712 | mS
| Magnet [4KV] |  | * | 2.538 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=800V] | t | 195 /197 | 195 /197 | µS | 195 / 192 | 195 / 195 | µS
| [C= 2µF] | Current | 31.0 /32.5 | 32.0 / 31.5 | A | 31.5 / 30.5 | 32.0 / 31.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION