## JI604
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER |  | F461
SUB CONTRACTOR : |  |  | JEUMONT SA |  | CONTRACT NUMBER |  | F461
COMPONENT NAME : |  |  | INNER LAYER
CERN PART NUMBER : |  |  | HCMB__A011 |  | Serial Number : |  | JI604
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | NON |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | JP MAGNIET
NAME OF RESPONSIBLE |  |  | JF.DE COENE
DATE OF TEST: |  |  | 2004-06-21 |  | TIME: |  | 0
Cable "I" Number : |  |  | 01B10546D
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 23.8 | °C
mV
| Inner LAYER |  |  |  | 497.2 | mW
| Inner LAYER[R20] |  |  |  | 490.1226 | mW
INDUCTANCE | [6 empty] | ITP step 4
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Inner LAYER |  |  | 10Hz | 1.94 | 0.242
|  |  |  | 100Hz | 1.91 | 2.26
|  |  |  | 1000Hz | 1.84 | 12.6
INSULATION RESISTANCE | [6 empty] | ITP step 6
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | >1000 | MW
| Right side |  |  |  | >1000 | MW
[V = 500V 30"]
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 5
V = 120Vturn |  |  |  | T | 258.67 | µS [Reference layer]
| Inner LAYER [1.8KV ; 10puls] |  |  | T | 260.34 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120Vturn
| Inner LAYER |  |  | C.side T |  | µS
| [1.8KV ; 10puls] |  |  | N.C. side T |  | µS
LHC/MMS TRACEABILITY INFORMATION