## JO597
ELECTRICAL TESTS OF LAYERS
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER |  | F461
SUB CONTRACTOR : |  |  | JEUMONT SA |  | CONTRACT NUMBER |  | F461
COMPONENT NAME |  |  | OUTER LAYER
CERN PART NUMBER : |  |  | HCMB__A012 |  | Serial Number : |  | JO597
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 3,4,5,6&9 |  | TEST NUMBER : |  | 3,4,5,et 6
NON CONFORMITY : |  |  | NON |  | NON-CONFORMITY NUMBER |  | <Number>
NAME OF TEST OPERATOR : |  |  | JP MAGNIET
NAME OF RESPONSIBLE |  |  | JF.DE COENE
DATE OF TEST: |  |  | 2004-06-15 |  | TIME: |  | 0
Cable "O" Number : |  |  | 02B50607H
R[dc] of the LAYER
I = | 1 | A |  |  |  |  | ITP step 3
Temp.* : | 28.5 | °C
mV
| Outer LAYER |  |  |  | 1040.9 | mW
| Outer LAYER[R20] |  |  |  | 1008.3309 | mW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 4
[5 empty] | L | Q
[mH]
| Outer LAYER |  |  | 10Hz | 6.67 | 0.399
|  |  |  | 100Hz | 6.67 | 3.87
|  |  |  | 1000Hz | 6.62 | 29.13
INSULATION RESISTANCE
| [Copper wedges] | [5 empty] | ITP step 6
| Left side |  |  |  | >1000 | MW
| Right side |  |  |  | >1000 | MW
[V = 500V 30"]
DISCHARGE TEST
[ Whithout Strain] | [6 empty] | ITP step 5
V = 120V/turn |  |  |  | T | 497.33 | µS [Reference layer]
| Outer LAYER [3.0KV ; 10puls] |  |  | T | 496.03 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 9
V = 120V/turn
| Outer LAYER |  |  | C.side T |  | µS
|  |  |  | N.C. side T |  | µS
[3.0KV ; 10puls]
LHC/MMS TRACEABILITY INFORMATION