## JP116
ELECTRICAL TESTS OF POLES
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : |  | F301
SUB CONTRACTOR : |  |  | JEUMONT INDUSTRIE |  | CONTRACT NUMBER : |  | F301
COMPONENT NAME : |  |  | POLE
CERN PART NUMBER : |  |  | HCMB__A010 |  | Serial Number : |  | JP 116
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 10,11,12,13,14,&14a |  | TEST NUMBER : |  | 10,11,12,13,14&14a
NON CONFORMITY : |  |  | NON |  | NON-CONFORMITY NUMBER : |  | <Number>
NAME OF TEST OPERATOR : |  |  | JP MAGNIET
NAME OF RESPONSIBLE : |  |  | JP.DELPLANCQ
DATE OF TEST: |  |  | 2002-06-27 |  | TIME: |  | 0
Cable "I" Number : |  |  | 01B10055D |  |  | Serial Number "I" | JI 118
Cable "O" Number : |  |  | 02B50081B |  |  | Serial Number "O" | JO 117
INSULATION RESISTANCE
Before splice soldering | [6 empty] | ITP step 10
INNER LAYER --> OUTER LAYER |  |  |  |  | >1000 | MW | >1000MW
[V= 1KV 30"]
R[dc] of the Pole
I = | 1 | A |  |  |  |  | ITP step 11
Temp.* : | 22.1 | °C |  |  |  | mV
| POLE |  |  |  | 1502.4 | mW
| POLE [R20] |  |  |  | 1490.5058 | mW
R[dc] of the Splice
I = | 10 | A |  |  |  |  | ITP step 12
Temp.* : | 35.3 | °C |  |  | 0.682 | mV
| Splice |  |  |  | 64.2669 | µW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 14a
[5 empty] | L | Q
[mH]
| POLE |  |  | 10Hz | 13.48 | 0.556
|  |  |  | 100Hz | 13.44 | 5.08
|  |  |  | 1000Hz | 12.87 | 17.04
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 13
V = 100V/turn |  |  |  | T | 696 | µS [Reference Pole]
| POLE | [4KV; 10 puls] |  | T | 692.04 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 14
V = 120V/turn
| POLE |  |  | C.side T |  | µS
|  |  |  | N.C. side T |  | µS
[4.8KV; 10 puls]
LHC/MMS TRACEABILITY INFORMATION