## 02P00219
ELECTRICAL TESTS OF POLES
LHC/MMS TRACEABILITY |  |  |  |  | INFORMATION
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : |  | F462
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER :
COMPONENT NAME : |  |  | POLE
CERN PART NUMBER : |  |  | HCMB__A0010 |  | Serial Number : |  | 02P00219
CERN INSPECTION & TEST PLAN NUMBER |  |  | ITP Step 10,11,12,13,14,&14a |  | TEST NUMBER : |  | 10,11,12,13,14&14a
NON CONFORMITY : |  |  | <No> |  | NON-CONFORMITY NUMBER : |  | <Number>
NAME OF TEST OPERATOR : |  |  | M.Levrero
NAME OF RESPONSIBLE : |  |  | Bruno Caserza
DATE OF TEST: |  |  | 2003-08-30 |  | TIME: |  | 8.3
Cable "I" Number : |  |  | 01B10239G |  |  | Serial Number "I" | 02I00222
Cable "O" Number : |  |  | 02K13501A |  |  | Serial Number "O" | 02E00222
INSULATION RESISTANCE
Before splice soldering | [6 empty] | ITP step 10
INNER LAYER --> OUTER LAYER |  |  |  |  | 137000 | MW | >1000MW
[V= 1KV 30"]
R[dc] of the Pole
I = | 1 | A |  |  |  |  | ITP step 11
Temp.* : | 23.5 | °C |  |  | 1548 | mV
| POLE |  |  |  | 1548 | mW
| POLE [R20] |  |  |  | 1527.6818 | mW
R[dc] of the Splice
I = | 30 | A |  |  |  |  | ITP step 12
Temp.* : | 25 | °C |  |  | 1.879 | mV
| Splice |  |  |  | 61.4052 | µW
INDUCTANCE
[Value from gain phase analyser] | [6 empty] | ITP step 14a
[5 empty] | L | Q
[mH]
| POLE |  |  | 10Hz | 14.32 | 0.574
|  |  |  | 100Hz | 14.08 | 4.79
|  |  |  | 1000Hz | 13.09 | 14.24
DISCHARGE TEST
Whitout Strain | [6 empty] | ITP step 13
V = 100V/turn |  |  |  | T | 1046 | µS [Reference Pole]
| POLE | [4KV; 10 puls] |  | T | 1052 | µS
[Whith Strain [120 N /mm2 straight part and the stress fades down in the ends] | [6 empty] | ITP step 14
V = 120V/turn
| POLE |  |  | C.side T | 1048 | µS
|  |  |  | N.C. side T | 1056 | µS
[4.8KV; 10 puls]
LHC/MMS TRACEABILITY INFORMATION