## N-3764P
ELECTRICAL TESTS OF POLES / Pole
LHC/MMS TRACEABILITY INFORMATION
MAIN CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | F489
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | ----
[5 empty] | SPECIFICATION: |  | LHC-MMS/98-198 Rev. 2.0
COMPONENT NAME : |  |  | POLE |  | BNN SERIAL NUMBER : |  | N-3764P
CERN PART NUMBER : |  |  | HCMB__A010 |  | Serial Number : |  | ----
BNN DOC ID NUMBER : |  |  | CF0015_C__N-3764P |  | BNN ORDER NUMBER : |  | N.911004
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 7a to 7e |  | TEST NUMBER : |  | 7
NON CONFORMITY : |  |  | <No> |  | NON-CONFORMITY NUMBER :
BNN SERIAL NUMBER INNER LAYER : |  |  | N-3764I |  | BNN SERIAL NUMBER OUTER LAYER : |  | N-3764E
NAME OF TEST OPERATOR : |  |  | see ITP steps |  | WORKING PLACE : |  | ON WOODEN TABLE
NAME OF RESPONSIBLE : |  |  | Zehner |  | BBP-SDA-CODE : |  | -----
DATE OF TEST : |  | (Starting) | 2004-06-28 |  | TIME : |  | -----
BNN INT. REG. NO : |  |  |  |  | DATE OF REPORT : |  | 2004-06-30
Cable "I" Number : |  |  | HCMB__A046-01E00091E |  | Serial Number "I" : |  | N-3764I
Cable "O" Number : |  |  | HCMB__A047-02G00272A |  | Serial Number "O" : |  | N-3764E
REQUIREMENTS OF TEST OBJECT/SPECIFICATION: |  |  |  | CERN: BNN: | LHC-MMS/98-198 Rev. 2.0 Annex B10 TABLE B Arbeitsanweisung CA0013_0
| INSULATION RESISTANCE |  | Date of Test: | 2004-06-28 | Equipment: | Megger BM21 [BM 00138]
| [Before splice soldering] |  | [V = 1KV; 30"] |  | NAME: | Zeuke | ITP step 7a
| INNER LAYER ----> OUTER LAYER |  |  |  | 326000 | MW | >1000MW
| R[dc] of the POLE |  | Date of Test: | 2004-06-30 | Equipment: | Kepco Power Supply [BM 00297], Testo 965 [BM 00116], HP34401A [BM 00294]
I = | 1 | A |  |  |  |  | ITP step 7b
Temp.* : | 26.5 | °C |  |  | 1561.5 | mV
| POLE |  |  |  | 1561.5 | mW | NAME:
| POLE [R20] |  |  |  | 1523.8606 | mW | Heymann
| R[dc] of the Splice |  | Date of Test: | 2004-06-28 | Equipment: | FUG Power Supply [BM 00325], Testo 965 [BM 00086], HP34401A [BM 00345]
I = | 30 | A |  |  |  |  | ITP step 7c
Temp.* : | 25.7 | °C |  |  | 2.11 | mV | NAME:
| Splice |  |  |  | 68.7655 | µW | Schmitt
| INDUCTANCE |  | Date of Test: | 2004-06-30 | Equipment: | Kepco Power Supply [BM 00297], Solartron Gain Phase Analyser [BM 00298]
| [Value from gain phase analyser] |  |  |  | L [mH] | Q | ITP step 7d
| POLE |  |  | 10Hz | 13.11 | 0.53601
|  |  |  | 100Hz | 13.07 | 4.9 | NAME:
|  |  |  | 1000Hz | 12.46 | 17.13 | Heymann
| DISCHARGE TEST |  | Date of Test: | 2004-06-30 | Equipment: | Seitz Impulse Tester [BM 00296]
| [Without Strain] |  | [V = 100V/turn; 4.0KV; 10puls] |  |  |  | ITP step 7e
|  |  |  | T | 984 | µS [Reference Pole]
| POLE |  |  | T | 984 | µS NAME: | Heymann
| [With Strain] |  | Date of Test:
| [120 N /mm2 straight part |  | [V = 120V/turn; 4.8KV; 10puls]
and the stress fades down in the ends] |  |  | Remark: This test can´t be executed due to the not available press provided by CERN
|  |  |  | C.side T | --------- | µS | (see annex E6)
| POLE |  |  | N.C. side T | --------- | µS NAME:
|  | test by |  | supervisor |  | approval
name |  | Heymann |  | Zehner |  | Zehner
company |  | BNM |  | BNN |  | BNN
date |  | 2004-06-30 |  | 2004-06-30 |  | 2004-07-01
signature
Note on H7: Bei einer Wiederholungs-messung ist der Revisions-buchstabe (z.B. A) direkt an die BNN SERIAL NUMBER anzuhängen, z.B. N-0245PA)!