## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.9701 | Magnet | 6.0991 | 6099.069 | 6050.6637 | 10 | 0.868 | 21.8 |  | 0.872 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.1065 | Aperture1 | 3.0536 | 3053.635 | 3029.3998 | 100 | 3.07 | 20.6 |  | 3.08 | 20.6
[9 empty] | YT121 | 21.7683 | Aperture2 | 3.0454 | 3045.403 | 3021.2331 | 1000 | 0.683 | 6.34 |  | 0.757 | 6.82
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.9125 | Apt1 Pup | 1.5285 | 1528.527 | 1516.3958
CERN PART NUMBER : |  |  | HCMBAL_A00101 |  | Serial Number : |  | 000094 |  | YT211 | 21.7773 | Apt1 Plw | 1.5251 | 1525.094 | 1512.9901 | 10 | 0.869 | 21.8 |  | 0.87 | 21.8
[9 empty] | YT212 | 21.9158 | Apt2 Pup | 1.5216 | 1521.634 | 1509.5575 | 100 | 3.06 | 20.5 |  | 3.08 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 21.9216 | Apt2 Plw | 1.5238 | 1523.751 | 1511.6577 | 1000 | 0.675 | 6.19 |  | 0.79 | 6.84
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.8652
[15 empty] | 10 | 0.872 | 43.7 |  | 0.874 | 43.7
NAME OF TEST OPERATOR: |  |  | HENRY/WENDEL | [11 empty] | 100 | 3.06 | 41.1 |  | 3.08 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.671 | 12.5 |  | 0.771 | 13.7
DATE OF TEST : |  |  | 2004-06-09 |  | TIME :
[15 empty] | 10 | 0.874 | 87.5
[15 empty] | 100 | 3.08 | 82.2
[15 empty] | 1000 | 0.717 | 26.2
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 22 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 50 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1528.527 | 1525.094 |  | 1521.634 | 1523.751
Poles [20°C] |  |  | 1516.3958 | 1512.9901 |  | 1509.5575 | 1511.6577
D1 & D2 |  |  | 3029.3998 | mW |  | 3021.2331 | mW
Magnet |  |  |  | 6050.6637 | mW
|  | Poles Nr. | JP 374 | JP 375 |  | JP 376 | JP 377
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.9701 | 21.7683 |  | 21.7773 | 21.9216
|  |  | 22.1065 | 21.9125 |  | 21.9158 | 21.8652
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 220 | nF |  | 230 | nF
D1 & D2 -----> Ground |  |  | 210 | nF |  | 210 | nF
Magnet -----> Ground |  |  |  | 350 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000094 |  |  |  |  | Date: | 2004-06-09
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.868 | 0.869 |  | 0.872 | 0.87
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.872 |  |  | 0.874
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.874
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.6 | 20.5
|  | (Q) | 3.07 | 3.06 |  | 3.06 | 3.08
D1 & D2 |  | (L) | 41.1 | mH |  | 41.1 | mH
|  | (Q) | 3.06 |  |  | 3.08
Magnet |  |  | (L) | 82.2 | mH
|  |  | (Q) | 3.08
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.34 | 6.19 |  | 6.82 | 6.84
|  | (Q) | 0.683 | 0.675 |  | 0.757 | 0.79
D1 & D2 |  | (L) | 12.5 | mH |  | 13.7 | mH
|  | (Q) | 0.671 |  |  | 0.771
Magnet |  |  | (L) | 26.2 | mH
|  |  | (Q) | 0.717
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000094 |  |  |  |  | Date: | 2004-06-09
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 11.4 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 23.6 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 2.54 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 2.4 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 6.6 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 5.55 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.952 | 0.95 |  | 0.944 | 0.952
Verification absence court-circuit entre spires sur chaque pole (comparaison entre chocs 1KV et 4KV)
|  |  | OK | OK |  | OK | OK
| Dipoles D1 & D2 [4KV] |  | 1.75 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.63 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000094 |  |  |  |  | Date: | 2004-06-09
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.9701 | 21.7683 |  |  | 21.7773 | 21.9216
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.1065 | 21.9125 |  |  | 21.9158 | 21.8652
Insulation Resistance
QHs -----> Masse |  | 4.62 |  | GW |  | 4.46 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 2.1 |  | GW |  | 1.92 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 6.3 | 6.45 | GW |  | 5.95 | 5.45 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 37.8 | 150 |  | YT 211 | 38.2 | 149
| YT 112 | 37.7 | 151 |  | YT 212 | 37.8 | 150
| YT 121 | 38 | 149 |  | YT 221 | 38 | 150
| YT 122 | 38.1 | 150 |  | YT 222 | 37.6 | 149
Insulation Resistance
QHs -----> Masse |  | 4.64 |  | GW |  | 4.48 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 2.28 |  | GW |  | 2.22 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 7.95 | 5.95 | GW |  | 5.6 | 5.1 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.95 | 21.76 |  |  | 21.77 | 21.92
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.08 | 21.92 |  |  | 21.93 | 21.87
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION