## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 22.5007 | Magnet | 6.0078 | 6007.771 | 6056.2208 | 10 | 0.888 | 21.8 |  | 0.89 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.485 | Aperture1 | 3.0048 | 3004.829 | 3029.0615 | 100 | 3.06 | 20.5 |  | 3.07 | 20.5
[9 empty] | YT121 | 21.589 | Aperture2 | 3.0029 | 3002.932 | 3027.1492 | 1000 | 0.652 | 6.13 |  | 0.751 | 6.76
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.596 | Apt1 Pup | 1.5031 | 1503.056 | 1515.1774
CERN PART NUMBER : |  |  | HCMBAL_A00101 |  | Serial Number : |  | 000095 |  | YT211 | 22.317 | Apt1 Plw | 1.5018 | 1501.757 | 1513.8679 | 10 | 0.888 | 21.8 |  | 0.888 | 21.8
[9 empty] | YT212 | 22.4952 | Apt2 Pup | 1.5016 | 1501.589 | 1513.6986 | 100 | 3.05 | 20.5 |  | 3.06 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 23.0128 | Apt2 Plw | 1.5013 | 1501.329 | 1513.4365 | 1000 | 0.646 | 6.06 |  | 0.791 | 6.82
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.7728
[15 empty] | 10 | 0.892 | 43.7 |  | 0.893 | 43.7
NAME OF TEST OPERATOR: |  |  | WENDEL | [11 empty] | 100 | 3.06 | 41 |  | 3.08 | 41
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.645 | 12.1 |  | 0.77 | 13.6
DATE OF TEST : |  |  | 23/01/2004 |  | TIME :
[15 empty] | 10 | 0.893 | 87.5
[15 empty] | 100 | 3.08 | 82
[15 empty] | 1000 | 0.704 | 25.7
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 18 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 28.2 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1503.056 | 1501.757 |  | 1501.589 | 1501.329
Poles [20°C] |  |  | 1515.1774 | 1513.8679 |  | 1513.6986 | 1513.4365
D1 & D2 |  |  | 3029.0615 | mW |  | 3027.1492 | mW
Magnet |  |  |  | 6056.2208 | mW
|  | Poles Nr. | JP 378 | JP 379 |  | JP 380 | JP 381
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 22.5007 | 21.589 |  | 22.317 | 23.0128
|  |  | 22.485 | 21.596 |  | 22.4952 | 22.7728
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 200 | nF |  | 190 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 330 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000095 |  |  |  |  | Date: | 23/01/2004
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.888 | 0.888 |  | 0.89 | 0.888
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.892 |  |  | 0.893
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.893
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.5 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.06 | 3.05 |  | 3.06 | 3.06
D1 & D2 |  | (L) | 41 | mH |  | 41 | mH
|  | (Q) | 3.06 |  |  | 3.08
Magnet |  |  | (L) | 82 | mH
|  |  | (Q) | 3.08
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.13 | 6.06 |  | 6.76 | 6.82
|  | (Q) | 0.652 | 0.646 |  | 0.751 | 0.791
D1 & D2 |  | (L) | 12.1 | mH |  | 13.6 | mH
|  | (Q) | 0.645 |  |  | 0.77
Magnet |  |  | (L) | 25.7 | mH
|  |  | (Q) | 0.704
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000095 |  |  |  |  | Date: | 23/01/2004
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.5007 | 21.589 |  |  | 22.317 | 23.0128
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.485 | 21.596 |  |  | 22.4952 | 22.7728
Insulation Resistance
QHs -----> Masse |  | 13.4 |  | GW |  | 20.8 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 7.5 |  | GW |  | 14.5 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 32.2 | 23.6 | GW |  | 49.2 | 50.5 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 36.6 | 153 |  | YT 211 | 37.2 | 151
| YT 112 | 37 | 152 |  | YT 212 | 36.6 | 153
| YT 121 | 37.8 | 146 |  | YT 221 | 35.7 | 156
| YT 122 | 38.4 | 146 |  | YT 222 | 36.4 | 153
Insulation Resistance
QHs -----> Masse |  | 24 |  | GW |  | 34.4 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 7.05 |  | GW |  | 13.6 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 35 | 22.8 | GW |  | 53.5 | 51.5 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.53 | 21.62 |  |  | 22.34 | 23.01
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.47 | 21.63 |  |  | 22.49 | 22.78
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000095 |  |  |  |  | Date: | 23/01/2004
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 41.8 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 45.6 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 7.85 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 18.4 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 14.9 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 26.8 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.96 | 0.944 |  | 0.96 | 0.944
| Dipoles D1 & D2 [4KV] |  | 1.75 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.62 | mS
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION