## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.715 | Magnet | 5.9707 | 5970.664 | 6006.7042 | 10 | 0.887 | 21.9 |  | 0.889 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 21.4156 | Aperture1 | 2.9826 | 2982.614 | 3000.6177 | 100 | 3.08 | 20.6 |  | 3.08 | 20.5
[9 empty] | YT121 | 21.2069 | Aperture2 | 2.988 | 2988.033 | 3006.0694 | 1000 | 0.668 | 6.25 |  | 0.746 | 6.7
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.3383 | Apt1 Pup | 1.492 | 1492.023 | 1501.0292
CERN PART NUMBER : |  |  | HCMBAL_A00101 |  | Serial Number : |  | 176 |  | YT211 | 21.362 | Apt1 Plw | 1.4906 | 1490.58 | 1499.5775 | 10 | 0.888 | 21.9 |  | 0.887 | 21.9
[9 empty] | YT212 | 21.0176 | Apt2 Pup | 1.4959 | 1495.869 | 1504.8984 | 100 | 3.06 | 20.5 |  | 3.08 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 21.7326 | Apt2 Plw | 1.4922 | 1492.151 | 1501.1579 | 1000 | 0.653 | 6.1 |  | 0.785 | 6.79
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.2269
[15 empty] | 10 | 0.892 | 43.8 |  | 0.891 | 43.8
NAME OF TEST OPERATOR: |  |  | GUTOWSKI / WENDEL | [11 empty] | 100 | 3.07 | 41.2 |  | 3.08 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.655 | 12.2 |  | 0.76 | 13.5
DATE OF TEST : |  |  | 19/10/2004 |  | TIME :
BAIE 2 | [14 empty] | 10 | 0.892 | 87.6
[15 empty] | 100 | 3.08 | 82.3
[15 empty] | 1000 | 0.704 | 25.7
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 18.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 58 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1492.023 | 1490.58 |  | 1495.869 | 1492.151
Poles [20°C] |  |  | 1501.0292 | 1499.5775 |  | 1504.8984 | 1501.1579
D1 & D2 |  |  | 3000.6177 | mW |  | 3006.0694 | mW
Magnet |  |  |  | 6006.7042 | mW
|  | Poles Nr. | JP 702 | JP 703 |  | JP 704 | JP 705
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.715 | 21.2069 |  | 21.362 | 21.7326
|  |  | 21.4156 | 21.3383 |  | 21.0176 | 21.2269
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 210 | nF |  | 210 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 330 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 176 |  |  |  |  | Date: | 19/10/2004
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.9 |  | 21.9 | 21.9
|  | (Q) | 0.887 | 0.888 |  | 0.889 | 0.887
D1 & D2 |  | (L) | 43.8 | mH |  | 43.8 | mH
|  | (Q) | 0.892 |  |  | 0.891
Magnet |  |  | (L) | 87.6 | mH
|  |  | (Q) | 0.892
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.08 | 3.06 |  | 3.07 | 3.08
D1 & D2 |  | (L) | 41.2 | mH |  | 41.1 | mH
|  | (Q) | 3.07 |  |  | 3.08
Magnet |  |  | (L) | 82.3 | mH
|  |  | (Q) | 3.08
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.25 | 6.1 |  | 6.7 | 6.79
|  | (Q) | 0.668 | 0.653 |  | 0.746 | 0.785
D1 & D2 |  | (L) | 12.2 | mH |  | 13.5 | mH
|  | (Q) | 0.655 |  |  | 0.76
Magnet |  |  | (L) | 25.7 | mH
|  |  | (Q) | 0.704
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 176 |  |  |  |  | Date: | 19/10/2004
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 28.8 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 16.8 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 4.4 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 5.15 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 9.25 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 9.85 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.3 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.948 | 0.956 |  | 0.96 | 0.95
Verification absence court-circuit entre spires sur chaque pole (comparaison entre chocs 1KV et 4KV)
|  |  | OK | OK |  | OK | OK
| Dipoles D1 & D2 [4KV] |  | 1.75 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.63 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 176 |  |  |  |  | Date: | 19/10/2004
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.715 | 21.2069 |  |  | 21.362 | 21.7326
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 21.4156 | 21.3383 |  |  | 21.0176 | 21.2269
Insulation Resistance
QHs -----> Masse |  | 6.15 |  | GW |  | 4.08 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 3.26 |  | GW |  | 3.22 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 9.15 | 11 | GW |  | 10.9 | 10.5 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 38 | 148 |  | YT 211 | 38.8 | 145
| YT 112 | 38.2 | 146 |  | YT 212 | 38.9 | 144
| YT 121 | 38.9 | 144 |  | YT 221 | 38.5 | 148
| YT 122 | 38.4 | 145 |  | YT 222 | 39.2 | 145
Insulation Resistance
QHs -----> Masse |  | 5.35 |  | GW |  | 5.9 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 3.38 |  | GW |  | 4 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 8.85 | 7.95 | GW |  | 11 | 7.4 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.77 | 21.25 |  |  | 21.41 | 21.79
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 21.55 | 21.38 |  |  | 21.08 | 21.28
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION