## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 22.6771 | Magnet | 6.0089 | 6008.917 | 5984.9771 | 10 | 0.881 | 21.9 |  | 0.881 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 21.9665 | Aperture1 | 3.0043 | 3004.332 | 2992.3625 | 100 | 3.06 | 20.5 |  | 3.06 | 20.5
[9 empty] | YT121 | 22.6718 | Aperture2 | 3.0046 | 3004.576 | 2992.6056 | 1000 | 0.654 | 6.14 |  | 0.74 | 6.66
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 22.1128 | Apt1 Pup | 1.5024 | 1502.413 | 1496.4273
CERN PART NUMBER : |  |  | HCMBAR_A00101 |  | Serial Number : |  | 000135 |  | YT211 | 22.4627 | Apt1 Plw | 1.5019 | 1501.918 | 1495.9343 | 10 | 0.88 | 21.8 |  | 0.88 | 21.8
[9 empty] | YT212 | 22.1242 | Apt2 Pup | 1.5028 | 1502.786 | 1496.7988 | 100 | 3.05 | 20.5 |  | 3.05 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 22.5861 | Apt2 Plw | 1.5018 | 1501.774 | 1495.7908 | 1000 | 0.647 | 6.07 |  | 0.778 | 6.79
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.2079
[15 empty] | 10 | 0.884 | 43.8 |  | 0.885 | 43.8
NAME OF TEST OPERATOR: |  |  | WENDEL/GUTOWSKI/JARDOT | [11 empty] | 100 | 3.06 | 41 |  | 3.06 | 41
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.645 | 12.2 |  | 0.753 | 13.4
DATE OF TEST : |  |  | 26/05/04 |  | TIME :
[15 empty] | 10 | 0.885 | 87.6
[15 empty] | 100 | 3.07 | 82.1
[15 empty] | 1000 | 0.691 | 25.4
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 21 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 35 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1502.413 | 1501.918 |  | 1502.786 | 1501.774
Poles [20°C] |  |  | 1496.4273 | 1495.9343 |  | 1496.7988 | 1495.7908
D1 & D2 |  |  | 2992.3625 | mW |  | 2992.6056 | mW
Magnet |  |  |  | 5984.9771 | mW
|  | Poles Nr. | JP 538 | JP 539 |  | JP 540 | JP 541
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 22.6771 | 22.6718 |  | 22.4627 | 22.5861
|  |  | 21.9665 | 22.1128 |  | 22.1242 | 22.2079
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 200 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 320 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000135 |  |  |  |  | Date: | 26/05/04
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.8 |  | 21.9 | 21.8
|  | (Q) | 0.881 | 0.88 |  | 0.881 | 0.88
D1 & D2 |  | (L) | 43.8 | mH |  | 43.8 | mH
|  | (Q) | 0.884 |  |  | 0.885
Magnet |  |  | (L) | 87.6 | mH
|  |  | (Q) | 0.885
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.5 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.06 | 3.05 |  | 3.06 | 3.05
D1 & D2 |  | (L) | 41 | mH |  | 41 | mH
|  | (Q) | 3.06 |  |  | 3.06
Magnet |  |  | (L) | 82.1 | mH
|  |  | (Q) | 3.07
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.14 | 6.07 |  | 6.66 | 6.79
|  | (Q) | 0.654 | 0.647 |  | 0.74 | 0.778
D1 & D2 |  | (L) | 12.2 | mH |  | 13.4 | mH
|  | (Q) | 0.645 |  |  | 0.753
Magnet |  |  | (L) | 25.4 | mH
|  |  | (Q) | 0.691
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000135 |  |  |  |  | Date: | 26/05/04
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 20.4 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 15.6 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 4.16 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 3.96 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 10.4 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 10.6 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.954 | 0.95 |  | 0.95 | 0.952
Verification absence court-circuit entre spires sur chaque pole (comparaison entre chocs 1KV et 4KV)
|  |  | OK | OK |  | OK | OK
| Dipoles D1 & D2 [4KV] |  | 1.75 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.63 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000135 |  |  |  |  | Date: | 26/05/04
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.6771 | 22.6718 |  |  | 22.4627 | 22.5861
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 21.9665 | 22.1128 |  |  | 22.1242 | 22.2079
Insulation Resistance
QHs -----> Masse |  | 32.6 |  | GW |  | 32.2 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 22.8 |  | GW |  | 24.8 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 75.5 | 73 | GW |  | 85.5 | 63.5 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 36.7 | 154 |  | YT 211 | 37.1 | 153
| YT 112 | 38 | 149 |  | YT 212 | 37.6 | 150
| YT 121 | 36.7 | 154 |  | YT 221 | 36.9 | 154
| YT 122 | 37 | 151 |  | YT 222 | 37.4 | 151
Insulation Resistance
QHs -----> Masse |  | 5.75 |  | GW |  | 5.65 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 4.14 |  | GW |  | 3.68 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 10.8 | 10.7 | GW |  | 10.9 | 10.7 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.71 | 22.71 |  |  | 22.53 | 22.64
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 21.99 | 22.16 |  |  | 22.18 | 22.24
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION