## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.3611 | Magnet | 5.9896 | 5989.57 | 6025.7243 | 10 | 0.888 | 21.8 |  | 0.889 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.2452 | Aperture1 | 2.9942 | 2994.245 | 3012.3189 | 100 | 3.07 | 20.5 |  | 3.09 | 20.5
[9 empty] | YT121 | 21.5419 | Aperture2 | 2.9953 | 2995.321 | 3013.4014 | 1000 | 0.757 | 6.96 |  | 0.801 | 7.14
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 22.3668 | Apt1 Pup | 1.4979 | 1497.948 | 1506.9899
CERN PART NUMBER : |  |  | HCMBA_A00101 |  | Serial Number : |  | 000082 |  | YT211 | 21.4934 | Apt1 Plw | 1.4963 | 1496.284 | 1505.3159 | 10 | 0.888 | 21.8 |  | 0.885 | 21.8
[9 empty] | YT212 | 22.2874 | Apt2 Pup | 1.4982 | 1498.172 | 1507.2153 | 100 | 3.07 | 20.4 |  | 3.07 | 20.4
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 21.4864 | Apt2 Plw | 1.4971 | 1497.132 | 1506.169 | 1000 | 0.759 | 6.9 |  | 0.82 | 7.1
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.3172
[15 empty] | 10 | 0.892 | 43.7 |  | 0.892 | 43.7
NAME OF TEST OPERATOR: |  |  | HENRY/JARDOT | [11 empty] | 100 | 3.08 | 41 |  | 3.1 | 41
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.755 | 13.9 |  | 0.808 | 14.2
DATE OF TEST : |  |  | 2003-04-12 |  | TIME :
[15 empty] | 10 | 0.892 | 87.4
[15 empty] | 100 | 3.1 | 81.9
[15 empty] | 1000 | 0.782 | 28.1
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 18.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 43 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1497.948 | 1496.284 |  | 1498.172 | 1497.132
Poles [20°C] |  |  | 1506.9899 | 1505.3159 |  | 1507.2153 | 1506.169
D1 & D2 |  |  | 3012.3189 | mW |  | 3013.4014 | mW
Magnet |  |  |  | 6025.7243 | mW
|  | Poles Nr. | JP 326 | JP 328 |  | JP 327 | JP 329
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.3611 | 21.5419 |  | 21.4934 | 21.4864
|  |  | 22.2452 | 22.3668 |  | 22.2874 | 22.3172
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 210 | nF |  | 210 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 330 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000082 |  |  |  |  | Date: | 2003-04-12
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.888 | 0.888 |  | 0.889 | 0.885
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.892 |  |  | 0.892
Magnet |  |  | (L) | 87.4 | mH
|  |  | (Q) | 0.892
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.5 | 20.4 |  | 20.5 | 20.4
|  | (Q) | 3.07 | 3.07 |  | 3.08 | 3.07
D1 & D2 |  | (L) | 41 | mH |  | 41 | mH
|  | (Q) | 3.08 |  |  | 3.1
Magnet |  |  | (L) | 81.9 | mH
|  |  | (Q) | 3.1
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.96 | 6.9 |  | 7.14 | 7.1
|  | (Q) | 0.757 | 0.759 |  | 0.801 | 0.82
D1 & D2 |  | (L) | 13.9 | mH |  | 14.2 | mH
|  | (Q) | 0.755 |  |  | 0.808
Magnet |  |  | (L) | 28.1 | mH
|  |  | (Q) | 0.782
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000082 |  |  |  |  | Date: | 2003-04-12
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 11.3 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 11.3 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 2.96 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 2.84 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 10.6 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 10.3 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.3 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.966 | 0.962 |  | 0.966 | 0.97
| Dipoles D1 & D2 [4KV] |  | 1.79 | mS |  | 1.79 | mS
| Magnet [4KV] |  |  | 2.7 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 448 | 456 | µS | 457 | 468 | µS
| [C= 2µF] | Current | 37.5 | 37.5 | A | 37 | 38 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION