## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 23.5998 | Magnet | 5.9737 | 5973.712 | 5985.6834 | 10 | 0.889 | 21.9 |  | 0.888 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 24.3522 | Aperture1 | 2.9872 | 2987.158 | 2993.1443 | 100 | 3.08 | 20.5 |  | 3.09 | 20.5
[9 empty] | YT121 | 24.0991 | Aperture2 | 2.9865 | 2986.544 | 2992.5291 | 1000 | 0.759 | 6.94 |  | 0.801 | 7.11
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 24.6386 | Apt1 Pup | 1.4908 | 1490.842 | 1493.8297
CERN PART NUMBER : |  |  | HCMBA_A00101 |  | Serial Number : |  | 000065 |  | YT211 | 24.5083 | Apt1 Plw | 1.4963 | 1496.303 | 1499.3016 | 10 | 0.884 | 21.8 |  | 0.885 | 21.8
[9 empty] | YT212 | 24.3935 | Apt2 Pup | 1.4935 | 1493.536 | 1496.5291 | 100 | 3.06 | 20.5 |  | 3.08 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 24.5617 | Apt2 Plw | 1.493 | 1492.987 | 1495.979 | 1000 | 0.765 | 6.9 |  | 0.826 | 7.09
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 24.4387
[15 empty] | 10 | 0.89 | 43.8 |  | 0.891 | 43.8
NAME OF TEST OPERATOR: |  |  | JARDOT | [11 empty] | 100 | 3.08 | 41 |  | 3.09 | 41
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.759 | 13.8 |  | 0.809 | 14.2
DATE OF TEST : |  |  | 25/11/2003 |  | TIME :
[15 empty] | 10 | 0.891 | 87.5
[15 empty] | 100 | 3.09 | 82.1
[15 empty] | 1000 | 0.782 | 27.9
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 44 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1490.842 | 1496.303 |  | 1493.536 | 1492.987
Poles [20°C] |  |  | 1493.8297 | 1499.3016 |  | 1496.5291 | 1495.979
D1 & D2 |  |  | 2993.1443 | mW |  | 2992.5291 | mW
Magnet |  |  |  | 5985.6834 | mW
|  | Poles Nr. | JP 258 | JP 261 |  | JP 259 | JP 260
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 23.5998 | 24.0991 |  | 24.5083 | 24.5617
|  |  | 24.3522 | 24.6386 |  | 24.3935 | 24.4387
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 190 | nF |  | 190 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 320 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000065 |  |  |  |  | Date: | 25/11/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.8 |  | 21.9 | 21.8
|  | (Q) | 0.889 | 0.884 |  | 0.888 | 0.885
D1 & D2 |  | (L) | 43.8 | mH |  | 43.8 | mH
|  | (Q) | 0.89 |  |  | 0.891
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.891
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.5 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.08 | 3.06 |  | 3.08 | 3.08
D1 & D2 |  | (L) | 41 | mH |  | 41 | mH
|  | (Q) | 3.08 |  |  | 3.09
Magnet |  |  | (L) | 82.1 | mH
|  |  | (Q) | 3.09
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.94 | 6.9 |  | 7.11 | 7.09
|  | (Q) | 0.759 | 0.765 |  | 0.801 | 0.826
D1 & D2 |  | (L) | 13.8 | mH |  | 14.2 | mH
|  | (Q) | 0.759 |  |  | 0.809
Magnet |  |  | (L) | 27.9 | mH
|  |  | (Q) | 0.782
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000065 |  |  |  |  | Date: | 25/11/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 23.2 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 21.6 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 14.3 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 14.8 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 37.2 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 32.4 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.3 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.3 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.4 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.4 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.966 | 0.972 |  | 0.972 | 0.97
| Dipoles D1 & D2 [4KV] |  | 1.8 | mS |  | 1.79 | mS
| Magnet [4KV] |  |  | 2.7 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 499 | 504 | µS | 516 | 529 | µS
| [C= 2µF] | Current | 36.5 | 37.5 | A | 35 | 36 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION