## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.0133 | Magnet | 5.981 | 5980.952 | 5992.9379 | 10 | 0.894 | 21.8 |  | 0.895 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 21.0273 | Aperture1 | 2.9909 | 2990.924 | 2996.9178 | 100 | 3.07 | 20.5 |  | 3.08 | 20.5
[9 empty] | YT121 | 21.048 | Aperture2 | 2.99 | 2990.024 | 2996.016 | 1000 | 0.755 | 6.91 |  | 0.795 | 7.04
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 20.8703 | Apt1 Pup | 1.496 | 1496.005 | 1499.003
CERN PART NUMBER : |  |  | HCMBAL_A00101 |  | Serial Number : |  | 000073 |  | YT211 | 21.1494 | Apt1 Plw | 1.4949 | 1494.911 | 1497.9068 | 10 | 0.894 | 21.8 |  | 0.891 | 21.8
[9 empty] | YT212 | 21.2365 | Apt2 Pup | 1.4948 | 1494.783 | 1497.7786 | 100 | 3.05 | 20.4 |  | 3.08 | 20.4
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.2453 | Apt2 Plw | 1.4952 | 1495.239 | 1498.2355 | 1000 | 0.763 | 6.87 |  | 0.82 | 7.03
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.2986
[15 empty] | 10 | 0.898 | 43.7 |  | 0.898 | 43.7
NAME OF TEST OPERATOR: |  |  | HENRY | [11 empty] | 100 | 3.07 | 40.9 |  | 3.09 | 40.9
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.754 | 13.8 |  | 0.806 | 14.1
DATE OF TEST : |  |  | 24/11/2003 |  | TIME :
[15 empty] | 10 | 0.899 | 87.4
[15 empty] | 100 | 3.09 | 81.9
[15 empty] | 1000 | 0.777 | 27.8
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 45 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1496.005 | 1494.911 |  | 1494.783 | 1495.239
Poles [20°C] |  |  | 1499.003 | 1497.9068 |  | 1497.7786 | 1498.2355
D1 & D2 |  |  | 2996.9178 | mW |  | 2996.016 | mW
Magnet |  |  |  | 5992.9379 | mW
|  | Poles Nr. | JP 290 | JP 291 |  | JP 292 | JP 293
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.0133 | 21.048 |  | 21.1494 | 20.2453
|  |  | 21.0273 | 20.8703 |  | 21.2365 | 20.2986
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 200 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 320 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000073 |  |  |  |  | Date: | 24/11/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.894 | 0.894 |  | 0.895 | 0.891
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.898 |  |  | 0.898
Magnet |  |  | (L) | 87.4 | mH
|  |  | (Q) | 0.899
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.5 | 20.4 |  | 20.5 | 20.4
|  | (Q) | 3.07 | 3.05 |  | 3.07 | 3.08
D1 & D2 |  | (L) | 40.9 | mH |  | 40.9 | mH
|  | (Q) | 3.07 |  |  | 3.09
Magnet |  |  | (L) | 81.9 | mH
|  |  | (Q) | 3.09
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.91 | 6.87 |  | 7.04 | 7.03
|  | (Q) | 0.755 | 0.763 |  | 0.795 | 0.82
D1 & D2 |  | (L) | 13.8 | mH |  | 14.1 | mH
|  | (Q) | 0.754 |  |  | 0.806
Magnet |  |  | (L) | 27.8 | mH
|  |  | (Q) | 0.777
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000073 |  |  |  |  | Date: | 24/11/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 12.8 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 13.4 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 3.44 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 3.66 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 13.1 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 14 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.5 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.3 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.4 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.2 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.96 | 0.938 |  | 0.934 | 0.968
| Dipoles D1 & D2 [4KV] |  | 1.76 | mS |  | 1.79 | mS
| Magnet [4KV] |  |  | 2.66 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 350 | 360 | µS | 345 | 340 | µS
| [C= 2µF] | Current | 40.5 | 41.5 | A | 40 | 39 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION