## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 26.2927 | Magnet | 5.9656 | 5965.591 | 6001.6006 | 10 | 0.895 | 21.9 |  | 0.894 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 25.0026 | Aperture1 | 2.9832 | 2983.172 | 3001.1791 | 100 | 3.07 | 20.5 |  | 3.08 | 20.5
[9 empty] | YT121 | 24.4744 | Aperture2 | 2.9824 | 2982.423 | 3000.4256 | 1000 | 0.756 | 6.89 |  | 0.796 | 7.02
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 24.383 | Apt1 Pup | 1.4913 | 1491.301 | 1500.3028
CERN PART NUMBER : |  |  | HCMBA_A00101 |  | Serial Number : |  | 000086 |  | YT211 | 25.1562 | Apt1 Plw | 1.4919 | 1491.863 | 1500.8682 | 10 | 0.892 | 21.8 |  | 0.892 | 21.9
[9 empty] | YT212 | 24.6818 | Apt2 Pup | 1.4918 | 1491.762 | 1500.7666 | 100 | 3.06 | 20.5 |  | 3.07 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 24.4418 | Apt2 Plw | 1.4907 | 1490.654 | 1499.6519 | 1000 | 0.76 | 6.84 |  | 0.819 | 7.01
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 24.3378
[15 empty] | 10 | 0.897 | 43.8 |  | 0.897 | 43.8
NAME OF TEST OPERATOR: |  |  | JARDOT/GUTOWSKI | [11 empty] | 100 | 3.07 | 41 |  | 3.09 | 41
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.754 | 13.7 |  | 0.803 | 14
DATE OF TEST : |  |  | 18/12/03 |  | TIME :
[15 empty] | 10 | 0.898 | 87.6
[15 empty] | 100 | 3.08 | 82.1
[15 empty] | 1000 | 0.778 | 27.7
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 18.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 32.5 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1491.301 | 1491.863 |  | 1491.762 | 1490.654
Poles [20°C] |  |  | 1500.3028 | 1500.8682 |  | 1500.7666 | 1499.6519
D1 & D2 |  |  | 3001.1791 | mW |  | 3000.4256 | mW
Magnet |  |  |  | 6001.6006 | mW
|  | Poles Nr. | JP 342 | JP 343 |  | JP 344 | JP 345
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 26.2927 | 24.4744 |  | 25.1562 | 24.4418
|  |  | 25.0026 | 24.383 |  | 24.6818 | 24.3378
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 190 | nF |  | 190 | nF
D1 & D2 -----> Ground |  |  | 190 | nF |  | 190 | nF
Magnet -----> Ground |  |  |  | 320 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000086 |  |  |  |  | Date: | 18/12/03
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.8 |  | 21.9 | 21.9
|  | (Q) | 0.895 | 0.892 |  | 0.894 | 0.892
D1 & D2 |  | (L) | 43.8 | mH |  | 43.8 | mH
|  | (Q) | 0.897 |  |  | 0.897
Magnet |  |  | (L) | 87.6 | mH
|  |  | (Q) | 0.898
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.5 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.07 | 3.06 |  | 3.07 | 3.07
D1 & D2 |  | (L) | 41 | mH |  | 41 | mH
|  | (Q) | 3.07 |  |  | 3.09
Magnet |  |  | (L) | 82.1 | mH
|  |  | (Q) | 3.08
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.89 | 6.84 |  | 7.02 | 7.01
|  | (Q) | 0.756 | 0.76 |  | 0.796 | 0.819
D1 & D2 |  | (L) | 13.7 | mH |  | 14 | mH
|  | (Q) | 0.754 |  |  | 0.803
Magnet |  |  | (L) | 27.7 | mH
|  |  | (Q) | 0.778
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000086 |  |  |  |  | Date: | 18/12/03
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 47.8 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 45.4 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 17.5 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 17.3 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 37.2 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 35 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.3 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.5 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.5 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.6 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.974 | 0.966 |  | 0.972 | 0.97
| Dipoles D1 & D2 [4KV] |  | 1.8 | mS |  | 1.79 | mS
| Magnet [4KV] |  |  | 2.7 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 520 | 494 | µS | 513 | 509 | µS
| [C= 2µF] | Current | 32.5 | 35 | A | 32.5 | 32.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION