## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 22.2341 | Magnet | 5.9821 | 5982.072 | 6006.0964 | 10 | 0.888 | 21.8 |  | 0.889 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.2929 | Aperture1 | 2.9881 | 2988.088 | 3000.0884 | 100 | 3.01 | 20.4 |  | 3.08 | 20.5
[9 empty] | YT121 | 22.0846 | Aperture2 | 2.994 | 2993.97 | 3005.994 | 1000 | 0.731 | 6.62 |  | 0.806 | 7.12
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.7972 | Apt1 Pup | 1.492 | 1491.965 | 1497.9568
CERN PART NUMBER : |  |  | HCMBA_A00101 |  | Serial Number : |  | 000090 |  | YT211 | 22.131 | Apt1 Plw | 1.4961 | 1496.11 | 1502.1185 | 10 | 0.887 | 21.8 |  | 0.888 | 21.9
[9 empty] | YT212 | 22.081 | Apt2 Pup | 1.4976 | 1497.622 | 1503.6365 | 100 | 3.03 | 20.4 |  | 3.07 | 20.4
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 23.5026 | Apt2 Plw | 1.4963 | 1496.33 | 1502.3394 | 1000 | 0.751 | 6.74 |  | 0.825 | 7.08
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 23.3869
[15 empty] | 10 | 0.891 | 43.7 |  | 0.892 | 43.7
NAME OF TEST OPERATOR: |  |  | JARDOT | [11 empty] | 100 | 3.03 | 40.8 |  | 3.09 | 40.9
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.745 | 13.4 |  | 0.814 | 14.2
DATE OF TEST : |  |  | 2004-09-01 |  | TIME :
[15 empty] | 10 | 0.892 | 87.4
[15 empty] | 100 | 3.06 | 81.8
[15 empty] | 1000 | 0.773 | 27.5
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 42 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1491.965 | 1496.11 |  | 1497.622 | 1496.33
Poles [20°C] |  |  | 1497.9568 | 1502.1185 |  | 1503.6365 | 1502.3394
D1 & D2 |  |  | 3000.0884 | mW |  | 3005.994 | mW
Magnet |  |  |  | 6006.0964 | mW
|  | Poles Nr. | JP 358 | JP 359 |  | JP 360 | JP 361
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 22.2341 | 22.0846 |  | 22.131 | 23.5026
|  |  | 22.2929 | 21.7972 |  | 22.081 | 23.3869
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 190 | nF |  | 190 | nF
D1 & D2 -----> Ground |  |  | 190 | nF |  | 190 | nF
Magnet -----> Ground |  |  |  | 320 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000090 |  |  |  |  | Date: | 2004-09-01
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.9 | 21.9
|  | (Q) | 0.888 | 0.887 |  | 0.889 | 0.888
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.891 |  |  | 0.892
Magnet |  |  | (L) | 87.4 | mH
|  |  | (Q) | 0.892
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.4 | 20.4 |  | 20.5 | 20.4
|  | (Q) | 3.01 | 3.03 |  | 3.03 | 3.07
D1 & D2 |  | (L) | 40.8 | mH |  | 40.9 | mH
|  | (Q) | 3.03 |  |  | 3.09
Magnet |  |  | (L) | 81.8 | mH
|  |  | (Q) | 3.06
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.62 | 6.74 |  | 7.12 | 7.08
|  | (Q) | 0.731 | 0.751 |  | 0.806 | 0.825
D1 & D2 |  | (L) | 13.4 | mH |  | 14.2 | mH
|  | (Q) | 0.745 |  |  | 0.814
Magnet |  |  | (L) | 27.5 | mH
|  |  | (Q) | 0.773
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000090 |  |  |  |  | Date: | 2004-09-01
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 24.8 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 31.4 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 19.7 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 20.8 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 34.6 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 38.6 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.4 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.4 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.966 | 0.97 |  | 0.974 | 0.974
| Dipoles D1 & D2 [4KV] |  | 1.79 | mS |  | 1.8 | mS
| Magnet [4KV] |  |  | 2.7 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 452 | 447 | µS | 467 | 464 | µS
| [C= 2µF] | Current | 36.5 | 36 | A | 36 | 34.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION