## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 22.8968 | Magnet | 5.9745 | 5974.456 | 5974.456 | 10 | 0.884 | 21.8 |  | 0.885 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.9221 | Aperture1 | 2.9873 | 2987.294 | 2987.294 | 100 | 3.06 | 20.5 |  | 3.07 | 20.5
[9 empty] | YT121 | 22.0392 | Aperture2 | 2.9871 | 2987.139 | 2987.139 | 1000 | 0.657 | 6.18 |  | 0.749 | 6.74
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 22.0057 | Apt1 Pup | 1.4945 | 1494.493 | 1494.493
CERN PART NUMBER : |  |  | HCMBAL_A00101 |  | Serial Number : |  | 000093 |  | YT211 | 22.6053 | Apt1 Plw | 1.4928 | 1492.769 | 1492.769 | 10 | 0.885 | 21.8 |  | 0.885 | 21.8
[9 empty] | YT212 | 22.5661 | Apt2 Pup | 1.4942 | 1494.22 | 1494.22 | 100 | 3.05 | 20.5 |  | 3.08 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 22.6215 | Apt2 Plw | 1.4929 | 1492.89 | 1492.89 | 1000 | 0.645 | 6.05 |  | 0.791 | 6.83
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.6398
[15 empty] | 10 | 0.889 | 43.7 |  | 0.889 | 43.7
NAME OF TEST OPERATOR: |  |  | GUTOWSKI / WENDEL | [11 empty] | 100 | 3.07 | 41 |  | 3.08 | 41
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.648 | 12.2 |  | 0.764 | 13.5
DATE OF TEST : |  |  | 16/01/2004 |  | TIME :
[15 empty] | 10 | 0.889 | 87.5
[15 empty] | 100 | 3.07 | 82.1
[15 empty] | 1000 | 0.699 | 25.6
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 20 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 37.6 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1494.493 | 1492.769 |  | 1494.22 | 1492.89
Poles [20°C] |  |  | 1494.493 | 1492.769 |  | 1494.22 | 1492.89
D1 & D2 |  |  | 2987.294 | mW |  | 2987.139 | mW
Magnet |  |  |  | 5974.456 | mW
|  | Poles Nr. | JP 370 | JP 371 |  | JP 372 | JP 373
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 22.8968 | 22.0392 |  | 22.6053 | 22.6215
|  |  | 22.9221 | 22.0057 |  | 22.5661 | 22.6398
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 190 | nF |  | 190 | nF
D1 & D2 -----> Ground |  |  | 190 | nF |  | 190 | nF
Magnet -----> Ground |  |  |  | 320 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000093 |  |  |  |  | Date: | 16/01/2004
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.884 | 0.885 |  | 0.885 | 0.885
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.889 |  |  | 0.889
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.889
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.5 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.06 | 3.05 |  | 3.07 | 3.08
D1 & D2 |  | (L) | 41 | mH |  | 41 | mH
|  | (Q) | 3.07 |  |  | 3.08
Magnet |  |  | (L) | 82.1 | mH
|  |  | (Q) | 3.07
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.18 | 6.05 |  | 6.74 | 6.83
|  | (Q) | 0.657 | 0.645 |  | 0.749 | 0.791
D1 & D2 |  | (L) | 12.2 | mH |  | 13.5 | mH
|  | (Q) | 0.648 |  |  | 0.764
Magnet |  |  | (L) | 25.6 | mH
|  |  | (Q) | 0.699
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000093 |  |  |  |  | Date: | 16/01/2004
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.8968 | 22.0392 |  |  | 22.6053 | 22.6215
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.9221 | 22.0057 |  |  | 22.5661 | 22.6398
Insulation Resistance
QHs -----> Masse |  | 16.8 |  | GW |  | 28 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 19.4 |  | GW |  | 25.2 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 71.5 | 77 | GW |  | 74.5 | 71.5 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 36.3 | 161 |  | YT 211 | 37 | 154
| YT 112 | 35.9 | 162 |  | YT 212 | 36.7 | 153
| YT 121 | 37.8 | 155 |  | YT 221 | 37.1 | 153
| YT 122 | 38 | 155 |  | YT 222 | 37 | 154
Insulation Resistance
QHs -----> Masse |  | 19.3 |  | GW |  | 36.8 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 22.2 |  | GW |  | 24 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 51 | 77 | GW |  | 74.5 | 70 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.92 | 22.08 |  |  | 22.65 | 22.67
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.95 | 22.06 |  |  | 22.61 | 22.69
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000093 |  |  |  |  | Date: | 16/01/2004
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 20.4 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 40.6 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 22.4 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 28.2 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 33.2 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 33.8 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.952 | 0.952 |  | 0.946 | 0.956
| Dipoles D1 & D2 [4KV] |  | 1.76 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.64 | mS
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION