## Sheet1
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 22.0205 | Magnet | 5.9874 | 5987.426 | 6011.4719 | 10 | 0.888 | 21.8 |  | 0.888 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.3758 | Aperture1 | 2.9937 | 2993.746 | 3005.7691 | 100 | 3.08 | 20.6 |  | 3.08 | 20.5
[9 empty] | YT121 | 21.8745 | Aperture2 | 2.9937 | 2993.67 | 3005.6928 | 1000 | 0.652 | 6.15 |  | 0.742 | 6.67
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 22.4058 | Apt1 Pup | 1.4975 | 1497.528 | 1503.5422
CERN PART NUMBER : |  |  | HCMBBL_A00101 |  | Serial Number : |  | 000098 |  | YT211 | 21.9284 | Apt1 Plw | 1.4962 | 1496.204 | 1502.2129 | 10 | 0.887 | 21.8 |  | 0.887 | 21.9
[9 empty] | YT212 | 22.4691 | Apt2 Pup | 1.4967 | 1496.716 | 1502.7269 | 100 | 3.07 | 20.5 |  | 3.07 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 21.9381 | Apt2 Plw | 1.4969 | 1496.926 | 1502.9378 | 1000 | 0.65 | 6.11 |  | 0.784 | 6.76
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.4716
[15 empty] | 10 | 0.892 | 43.8 |  | 0.891 | 43.8
NAME OF TEST OPERATOR: |  |  | GUTOWSKI / WENDEL | [11 empty] | 100 | 3.09 | 41.1 |  | 3.08 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.646 | 12.2 |  | 0.765 | 13.6
DATE OF TEST : |  |  | 2004-02-11 |  | TIME :
[15 empty] | 10 | 0.892 | 87.5
[15 empty] | 100 | 3.09 | 82.2
[15 empty] | 1000 | 0.698 | 25.6
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 37 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1497.528 | 1496.204 |  | 1496.716 | 1496.926
Poles [20°C] |  |  | 1503.5422 | 1502.2129 |  | 1502.7269 | 1502.9378
D1 & D2 |  |  | 3005.7691 | mW |  | 3005.6928 | mW
Magnet |  |  |  | 6011.4719 | mW
|  | Poles Nr. | JP 390 | JP 391 |  | JP 392 | JP 393
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 22.0205 | 21.8745 |  | 21.9284 | 21.9381
|  |  | 22.3758 | 22.4058 |  | 22.4691 | 22.4716
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 200 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 320 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000098 |  |  |  |  | Date: | 2004-02-11
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.9 | 21.9
|  | (Q) | 0.888 | 0.887 |  | 0.888 | 0.887
D1 & D2 |  | (L) | 43.8 | mH |  | 43.8 | mH
|  | (Q) | 0.892 |  |  | 0.891
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.892
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.08 | 3.07 |  | 3.09 | 3.07
D1 & D2 |  | (L) | 41.1 | mH |  | 41.1 | mH
|  | (Q) | 3.09 |  |  | 3.08
Magnet |  |  | (L) | 82.2 | mH
|  |  | (Q) | 3.09
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.15 | 6.11 |  | 6.67 | 6.76
|  | (Q) | 0.652 | 0.65 |  | 0.742 | 0.784
D1 & D2 |  | (L) | 12.2 | mH |  | 13.6 | mH
|  | (Q) | 0.646 |  |  | 0.765
Magnet |  |  | (L) | 25.6 | mH
|  |  | (Q) | 0.698
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000098 |  |  |  |  | Date: | 2004-02-11
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 13.8 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 17.4 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 5.5 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 5.75 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 15.4 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 12.7 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.958 | 0.954 |  | 0.946 | 0.962
| Dipoles D1 & D2 [4KV] |  | 1.76 | mS |  | 1.77 | mS
| Magnet [4KV] |  |  | 2.64 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000098 |  |  |  |  | Date: | 2004-02-11
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.0205 | 21.8745 |  |  | 21.9284 | 21.9381
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.3758 | 22.4058 |  |  | 22.4691 | 22.4716
Insulation Resistance
QHs -----> Masse |  | 7.65 |  | GW |  | 7.3 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 4.6 |  | GW |  | 4.48 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 18 | 15.2 | GW |  | 15 | 15.3 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 37.8 | 149 |  | YT 211 | 37.7 | 149
| YT 112 | 37.2 | 152 |  | YT 212 | 36.7 | 152
| YT 121 | 37.8 | 149 |  | YT 221 | 38.1 | 149
| YT 122 | 36.7 | 152 |  | YT 222 | 36.6 | 152
Insulation Resistance
QHs -----> Masse |  | 7.55 |  | GW |  | 7.2 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 5.25 |  | GW |  | 5.5 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 18.3 | 15.2 | GW |  | 15.1 | 15.3 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.01 | 21.88 |  |  | 21.95 | 21.95
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.37 | 22.42 |  |  | 22.48 | 22.48