## Coll.102
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.9839 | Magnet | 5.9815 | 5981.499 | 5976.7176 | 10 | 0.887 | 21.9 |  | 0.888 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 21.8442 | Aperture1 | 2.989 | 2989.013 | 2986.6237 | 100 | 3.09 | 20.6 |  | 3.1 | 20.6
[9 empty] | YT121 | 21.0499 | Aperture2 | 2.9925 | 2992.477 | 2990.0849 | 1000 | 0.662 | 6.24 |  | 0.756 | 6.84
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.0493 | Apt1 Pup | 1.495 | 1495.013 | 1493.8179
CERN PART NUMBER : |  |  | HCMBBL_A00101 |  | Serial Number : |  | 000102 |  | YT211 | 21.3756 | Apt1 Plw | 1.494 | 1493.984 | 1492.7898 | 10 | 0.887 | 21.9 |  | 0.886 | 21.9
[9 empty] | YT212 | 20.7313 | Apt2 Pup | 1.4963 | 1496.305 | 1495.1089 | 100 | 3.08 | 20.5 |  | 3.1 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.7107 | Apt2 Plw | 1.4962 | 1496.157 | 1494.961 | 1000 | 0.657 | 6.17 |  | 0.797 | 6.89
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.3465
[15 empty] | 10 | 0.891 | 43.8 |  | 0.89 | 43.8
NAME OF TEST OPERATOR: |  |  | HENRY / WENDEL | [11 empty] | 100 | 3.09 | 41.2 |  | 3.1 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.655 | 12.4 |  | 0.769 | 13.7
DATE OF TEST : |  |  | 2004-06-04 |  | TIME :
[15 empty] | 10 | 0.892 | 87.6
[15 empty] | 100 | 3.1 | 82.3
[15 empty] | 1000 | 0.706 | 26.1
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 20.2 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 32.2 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1495.013 | 1493.984 |  | 1496.305 | 1496.157
Poles [20°C] |  |  | 1493.8179 | 1492.7898 |  | 1495.1089 | 1494.961
D1 & D2 |  |  | 2986.6237 | mW |  | 2990.0849 | mW
Magnet |  |  |  | 5976.7176 | mW
|  | Poles Nr. | JP 406 | JP 407 |  | JP 408 | JP 409
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.9839 | 21.0499 |  | 21.3756 | 20.7107
|  |  | 21.8442 | 21.0493 |  | 20.7313 | 20.3465
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 210 | nF |  | 210 | nF
D1 & D2 -----> Ground |  |  | 210 | nF |  | 210 | nF
Magnet -----> Ground |  |  |  | 350 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000102 |  |  |  |  | Date: | 2004-06-04
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.9 |  | 21.9 | 21.9
|  | (Q) | 0.887 | 0.887 |  | 0.888 | 0.886
D1 & D2 |  | (L) | 43.8 | mH |  | 43.8 | mH
|  | (Q) | 0.891 |  |  | 0.89
Magnet |  |  | (L) | 87.6 | mH
|  |  | (Q) | 0.892
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.6 | 20.5
|  | (Q) | 3.09 | 3.08 |  | 3.09 | 3.1
D1 & D2 |  | (L) | 41.2 | mH |  | 41.1 | mH
|  | (Q) | 3.09 |  |  | 3.1
Magnet |  |  | (L) | 82.3 | mH
|  |  | (Q) | 3.1
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.24 | 6.17 |  | 6.84 | 6.89
|  | (Q) | 0.662 | 0.657 |  | 0.756 | 0.797
D1 & D2 |  | (L) | 12.4 | mH |  | 13.7 | mH
|  | (Q) | 0.655 |  |  | 0.769
Magnet |  |  | (L) | 26.1 | mH
|  |  | (Q) | 0.706
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000102 |  |  |  |  | Date: | 2004-06-04
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 52.5 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 48.8 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 31.6 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 29.2 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 14.9 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 29.4 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.2 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.2 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.2 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.948 | 0.954 |  | 0.952 | 0.95
| Dipoles D1 & D2 [4KV] |  | 1.75 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.63 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000102 |  |  |  |  | Date: | 2004-06-04
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.9839 | 21.0499 |  |  | 21.3756 | 20.7107
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 21.8442 | 21.0493 |  |  | 20.7313 | 20.3465
Insulation Resistance
QHs -----> Masse |  | 45 |  | GW |  | 38.6 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 21.8 |  | GW |  | 20.6 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 68.5 | 64.5 | GW |  | 62 | 84 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 38 | 149 |  | YT 211 | 38.9 | 145
| YT 112 | 37.8 | 148 |  | YT 212 | 40.2 | 141
| YT 121 | 39.2 | 143 |  | YT 221 | 40 | 141
| YT 122 | 39.3 | 143 |  | YT 222 | 41 | 138
Insulation Resistance
QHs -----> Masse |  | 47.2 |  | GW |  | 40.6 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 26.6 |  | GW |  | 24.8 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 77.5 | 91.5 | GW |  | 66 | 83.5 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.98 | 21.06 |  |  | 21.39 | 20.72
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 21.8 | 21.06 |  |  | 20.73 | 20.31