## Sheet1
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.6606 | Magnet | 5.976 | 5975.964 | 5999.9639 | 10 | 0.888 | 21.9 |  | 0.889 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.2225 | Aperture1 | 2.9882 | 2988.168 | 3000.1687 | 100 | 3.08 | 20.6 |  | 3.1 | 20.5
[9 empty] | YT121 | 21.0307 | Aperture2 | 2.9878 | 2987.761 | 2999.76 | 1000 | 0.667 | 6.29 |  | 0.753 | 6.83
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.8475 | Apt1 Pup | 1.4953 | 1495.252 | 1501.257
CERN PART NUMBER : |  |  | HCMBBL_A00101 |  | Serial Number : |  | 000104 |  | YT211 | 20.8338 | Apt1 Plw | 1.4929 | 1492.885 | 1498.8805 | 10 | 0.888 | 21.9 |  | 0.887 | 21.9
[9 empty] | YT212 | 21.0172 | Apt2 Pup | 1.4933 | 1493.259 | 1499.256 | 100 | 3.08 | 20.5 |  | 3.1 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.8142 | Apt2 Plw | 1.4945 | 1494.456 | 1500.4578 | 1000 | 0.657 | 6.2 |  | 0.794 | 6.87
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.0402
[15 empty] | 10 | 0.892 | 43.8 |  | 0.891 | 43.8
NAME OF TEST OPERATOR: |  |  | GUTOWSKI / JARDOT | [11 empty] | 100 | 3.09 | 41.1 |  | 3.1 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.653 | 12.4 |  | 0.766 | 13.6
DATE OF TEST : |  |  | 26/02/2004 |  | TIME :
[15 empty] | 10 | 0.892 | 87.5
[15 empty] | 100 | 3.1 | 82.2
[15 empty] | 1000 | 0.709 | 26
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 21 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1495.252 | 1492.885 |  | 1493.259 | 1494.456
Poles [20°C] |  |  | 1501.257 | 1498.8805 |  | 1499.256 | 1500.4578
D1 & D2 |  |  | 3000.1687 | mW |  | 2999.76 | mW
Magnet |  |  |  | 5999.9639 | mW
|  | Poles Nr. | JP 414 | JP 416 |  | JP 415 | JP 417
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.6606 | 21.0307 |  | 20.8338 | 20.8142
|  |  | 22.2225 | 21.8475 |  | 21.0172 | 21.0402
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 190 | nF |  | 190 | nF
D1 & D2 -----> Ground |  |  | 180 | nF |  | 180 | nF
Magnet -----> Ground |  |  |  | 290 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000104 |  |  |  |  | Date: | 26/02/2004
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.9 |  | 21.9 | 21.9
|  | (Q) | 0.888 | 0.888 |  | 0.889 | 0.887
D1 & D2 |  | (L) | 43.8 | mH |  | 43.8 | mH
|  | (Q) | 0.892 |  |  | 0.891
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.892
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.08 | 3.08 |  | 3.09 | 3.1
D1 & D2 |  | (L) | 41.1 | mH |  | 41.1 | mH
|  | (Q) | 3.09 |  |  | 3.1
Magnet |  |  | (L) | 82.2 | mH
|  |  | (Q) | 3.1
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.29 | 6.2 |  | 6.83 | 6.87
|  | (Q) | 0.667 | 0.657 |  | 0.753 | 0.794
D1 & D2 |  | (L) | 12.4 | mH |  | 13.6 | mH
|  | (Q) | 0.653 |  |  | 0.766
Magnet |  |  | (L) | 26 | mH
|  |  | (Q) | 0.709
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000104 |  |  |  |  | Date: | 26/02/2004
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 60.5 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 52 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 28.6 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 29 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 32.4 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 34.2 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.948 | 0.946 |  | 0.948 | 0.95
| Dipoles D1 & D2 [4KV] |  | 1.75 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.62 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000104 |  |  |  |  | Date: | 26/02/2004
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.6606 | 21.0307 |  |  | 20.8338 | 20.8142
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.2225 | 21.8475 |  |  | 21.0172 | 21.0402
Insulation Resistance
QHs -----> Masse |  | 50.5 |  | GW |  | 48 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 24.2 |  | GW |  | 21.2 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 87.5 | 85.5 | GW |  | 73 | 83.5 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 38.5 | 147 |  | YT 211 | 39.6 | 141
| YT 112 | 37.6 | 150 |  | YT 212 | 39.7 | 142
| YT 121 | 39.5 | 142 |  | YT 221 | 40.1 | 141
| YT 122 | 37.6 | 148 |  | YT 222 | 39.3 | 143
Insulation Resistance
QHs -----> Masse |  | 53.5 |  | GW |  | 49 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 28.2 |  | GW |  | 27 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 78 | 87.5 | GW |  | 82.5 | 83 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.63 | 21 |  |  | 20.79 | 20.75
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.14 | 21.84 |  |  | 20.96 | 21