## Sheet1
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.5719 | Magnet | 5.9549 | 5954.866 | 5907.6052 | 10 | 0.89 | 21.8 |  | 0.89 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.3835 | Aperture1 | 2.9759 | 2975.927 | 2952.3085 | 100 | 3.09 | 20.5 |  | 3.1 | 20.5
[9 empty] | YT121 | 21.7395 | Aperture2 | 2.9789 | 2978.93 | 2955.2877 | 1000 | 0.656 | 6.2 |  | 0.749 | 6.77
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 22.2936 | Apt1 Pup | 1.4883 | 1488.345 | 1476.5327
CERN PART NUMBER : |  |  | HCMBBL_A00101 |  | Serial Number : |  | 000106 |  | YT211 | 21.5666 | Apt1 Plw | 1.4876 | 1487.569 | 1475.7629 | 10 | 0.89 | 21.8 |  | 0.889 | 21.8
[9 empty] | YT212 | 22.304 | Apt2 Pup | 1.4904 | 1490.39 | 1478.5615 | 100 | 3.08 | 20.5 |  | 3.09 | 20.4
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 21.9141 | Apt2 Plw | 1.4885 | 1488.527 | 1476.7133 | 1000 | 0.65 | 6.13 |  | 0.785 | 6.82
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.5407
[15 empty] | 10 | 0.893 | 43.7 |  | 0.893 | 43.7
NAME OF TEST OPERATOR: |  |  | GUTOWSKI / WENDEL/JARDOT | [11 empty] | 100 | 3.08 | 41.1 |  | 3.1 | 41
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.65 | 12.4 |  | 0.767 | 13.7
DATE OF TEST : |  |  | 23/03/2004 |  | TIME :
[15 empty] | 10 | 0.893 | 87.4
[15 empty] | 100 | 3.11 | 82.1
[15 empty] | 1000 | 0.704 | 25.9
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 22 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 31.7 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1488.345 | 1487.569 |  | 1490.39 | 1488.527
Poles [20°C] |  |  | 1476.5327 | 1475.7629 |  | 1478.5615 | 1476.7133
D1 & D2 |  |  | 2952.3085 | mW |  | 2955.2877 | mW
Magnet |  |  |  | 5907.6052 | mW
|  | Poles Nr. | JP 422 | JP 423 |  | JP 424 | JP 425
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.5719 | 21.7395 |  | 21.5666 | 21.9141
|  |  | 22.3835 | 22.2936 |  | 22.304 | 22.5407
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 200 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 330 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000106 |  |  |  |  | Date: | 23/03/2004
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.89 | 0.89 |  | 0.89 | 0.889
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.893 |  |  | 0.893
Magnet |  |  | (L) | 87.4 | mH
|  |  | (Q) | 0.893
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.5 | 20.5 |  | 20.5 | 20.4
|  | (Q) | 3.09 | 3.08 |  | 3.08 | 3.09
D1 & D2 |  | (L) | 41.1 | mH |  | 41 | mH
|  | (Q) | 3.08 |  |  | 3.1
Magnet |  |  | (L) | 82.1 | mH
|  |  | (Q) | 3.11
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.2 | 6.13 |  | 6.77 | 6.82
|  | (Q) | 0.656 | 0.65 |  | 0.749 | 0.785
D1 & D2 |  | (L) | 12.4 | mH |  | 13.7 | mH
|  | (Q) | 0.65 |  |  | 0.767
Magnet |  |  | (L) | 25.9 | mH
|  |  | (Q) | 0.704
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000106 |  |  |  |  | Date: | 23/03/2004
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 17 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 21.8 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 5.45 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 7.05 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 14.3 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 14.7 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.2 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.954 | 0.954 |  | 0.95 | 0.95
| Dipoles D1 & D2 [4KV] |  | 1.74 | mS |  | 1.75 | mS
| Magnet [4KV] |  |  | 2.62 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000106 |  |  |  |  | Date: | 23/03/2004
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.5719 | 21.7395 |  |  | 21.5666 | 21.9141
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.3835 | 22.2936 |  |  | 22.304 | 22.5407
Insulation Resistance
QHs -----> Masse |  | 6.95 |  | GW |  | 7.45 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 4.04 |  | GW |  | 4.26 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 15.2 | 14.7 | GW |  | 15 | 17 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 38.3 | 146 |  | YT 211 | 38.8 | 146
| YT 112 | 37.1 | 151 |  | YT 212 | 36.9 | 152
| YT 121 | 38 | 148 |  | YT 221 | 37.6 | 149
| YT 122 | 37.1 | 151 |  | YT 222 | 36.7 | 153
Insulation Resistance
QHs -----> Masse |  | 6.7 |  | GW |  | 7.2 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 5.15 |  | GW |  | 5.7 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 15.5 | 14.8 | GW |  | 14.7 | 16.7 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.54 | 21.73 |  |  | 21.54 | 21.9
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.36 | 22.31 |  |  | 22.29 | 22.52