## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 22.418 | Magnet | 6.0131 | 6013.142 | 6001.1397 | 10 | 0.883 | 21.8 |  | 0.882 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.6757 | Aperture1 | 3.0052 | 3005.211 | 2999.2126 | 100 | 3.08 | 20.6 |  | 3.1 | 20.5
[9 empty] | YT121 | 22.5215 | Aperture2 | 3.0079 | 3007.929 | 3001.9251 | 1000 | 0.659 | 6.24 |  | 0.747 | 6.82
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 22.7808 | Apt1 Pup | 1.502 | 1502.021 | 1499.023
CERN PART NUMBER : |  |  | HCMBBL_A00101 |  | Serial Number : |  | 000107 |  | YT211 | 22.3803 | Apt1 Plw | 1.5032 | 1503.188 | 1500.1876 | 10 | 0.882 | 21.8 |  | 0.881 | 21.8
[9 empty] | YT212 | 22.6615 | Apt2 Pup | 1.5043 | 1504.3 | 1501.2974 | 100 | 3.07 | 20.5 |  | 3.1 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 22.4075 | Apt2 Plw | 1.5036 | 1503.623 | 1500.6218 | 1000 | 0.645 | 6.11 |  | 0.785 | 6.88
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.7145
[15 empty] | 10 | 0.886 | 43.8 |  | 0.885 | 43.7
NAME OF TEST OPERATOR: |  |  | HENRY/WENDEL | [11 empty] | 100 | 3.09 | 41.1 |  | 3.09 | 41
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.644 | 12.3 |  | 0.759 | 13.6
DATE OF TEST : |  |  | 2004-09-04 |  | TIME :
[15 empty] | 10 | 0.886 | 87.5
[15 empty] | 100 | 3.09 | 82.2
[15 empty] | 1000 | 0.701 | 26
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 20.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 27 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1502.021 | 1503.188 |  | 1504.3 | 1503.623
Poles [20°C] |  |  | 1499.023 | 1500.1876 |  | 1501.2974 | 1500.6218
D1 & D2 |  |  | 2999.2126 | mW |  | 3001.9251 | mW
Magnet |  |  |  | 6001.1397 | mW
|  | Poles Nr. | JP 426 | JP 429 |  | JP 427 | JP 428
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 22.418 | 22.5215 |  | 22.3803 | 22.4075
|  |  | 22.6757 | 22.7808 |  | 22.6615 | 22.7145
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 190 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 190 | nF |  | 190 | nF
Magnet -----> Ground |  |  |  | 320 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000107 |  |  |  |  | Date: | 2004-09-04
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.883 | 0.882 |  | 0.882 | 0.881
D1 & D2 |  | (L) | 43.8 | mH |  | 43.7 | mH
|  | (Q) | 0.886 |  |  | 0.885
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.886
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.08 | 3.07 |  | 3.09 | 3.1
D1 & D2 |  | (L) | 41.1 | mH |  | 41 | mH
|  | (Q) | 3.09 |  |  | 3.09
Magnet |  |  | (L) | 82.2 | mH
|  |  | (Q) | 3.09
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.24 | 6.11 |  | 6.82 | 6.88
|  | (Q) | 0.659 | 0.645 |  | 0.747 | 0.785
D1 & D2 |  | (L) | 12.3 | mH |  | 13.6 | mH
|  | (Q) | 0.644 |  |  | 0.759
Magnet |  |  | (L) | 26 | mH
|  |  | (Q) | 0.701
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000107 |  |  |  |  | Date: | 2004-09-04
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 18.7 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 18.3 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 5.1 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 6 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 12.6 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 14.4 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.2 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.956 | 0.958 |  | 0.956 | 0.956
| Dipoles D1 & D2 [4KV] |  | 1.76 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.64 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000107 |  |  |  |  | Date: | 2004-09-04
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.418 | 22.5215 |  |  | 22.3803 | 22.4075
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.6757 | 22.7808 |  |  | 22.6615 | 22.7145
Insulation Resistance
QHs -----> Masse |  | 5.1 |  | GW |  | 5.45 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 4.1 |  | GW |  | 4.96 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 15.7 | 14.6 | GW |  | 16.3 | 16.3 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 36.6 | 153 |  | YT 211 | 37 | 152
| YT 112 | 36.9 | 154 |  | YT 212 | 36.6 | 154
| YT 121 | 37 | 153 |  | YT 221 | 37 | 153
| YT 122 | 36 | 154 |  | YT 222 | 36.8 | 154
Insulation Resistance
QHs -----> Masse |  | 7.05 |  | GW |  | 9.85 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 5.15 |  | GW |  | 4.58 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 15.7 | 14.4 | GW |  | 15.8 | 15.8 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.46 | 22.55 |  |  | 22.43 | 22.46
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.7 | 22.81 |  |  | 22.71 | 22.7
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION