## Coll.0117
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 22.0223 | Magnet | 5.997 | 5997.036 | 5985.0659 | 10 | 0.885 | 21.8 |  | 0.886 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.4888 | Aperture1 | 2.9995 | 2999.499 | 2993.512 | 100 | 3.08 | 20.6 |  | 3.08 | 20.5
[9 empty] | YT121 | 22.1604 | Aperture2 | 2.9975 | 2997.539 | 2991.5559 | 1000 | 0.656 | 6.2 |  | 0.738 | 6.71
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 22.5376 | Apt1 Pup | 1.501 | 1501 | 1498.004
CERN PART NUMBER : |  |  | HCMBBL_A00101 |  | Serial Number : |  | 000117 |  | YT211 | 21.7675 | Apt1 Plw | 1.4985 | 1498.491 | 1495.5 | 10 | 0.885 | 21.8 |  | 0.885 | 21.8
[9 empty] | YT212 | 22.2635 | Apt2 Pup | 1.4987 | 1498.658 | 1495.6667 | 100 | 3.08 | 20.5 |  | 3.07 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 22.1278 | Apt2 Plw | 1.4989 | 1498.871 | 1495.8792 | 1000 | 0.649 | 6.09 |  | 0.777 | 6.8
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.6073
[15 empty] | 10 | 0.889 | 43.8 |  | 0.889 | 43.8
NAME OF TEST OPERATOR: |  |  | JARDOT / WENDEL | [11 empty] | 100 | 3.08 | 41.1 |  | 3.08 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.649 | 12.3 |  | 0.753 | 13.5
DATE OF TEST : |  |  | 30/03/2004 |  | TIME :
[15 empty] | 10 | 0.89 | 87.5
[15 empty] | 100 | 3.09 | 82.3
[15 empty] | 1000 | 0.701 | 25.8
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 20.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 22 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1501 | 1498.491 |  | 1498.658 | 1498.871
Poles [20°C] |  |  | 1498.004 | 1495.5 |  | 1495.6667 | 1495.8792
D1 & D2 |  |  | 2993.512 | mW |  | 2991.5559 | mW
Magnet |  |  |  | 5985.0659 | mW
|  | Poles Nr. | JP 466 | JP 467 |  | JP 468 | JP 469
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 22.0223 | 22.1604 |  | 21.7675 | 22.1278
|  |  | 22.4888 | 22.5376 |  | 22.2635 | 22.6073
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 220 | nF |  | 220 | nF
D1 & D2 -----> Ground |  |  | 210 | nF |  | 220 | nF
Magnet -----> Ground |  |  |  | 360 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000117 |  |  |  |  | Date: | 30/03/2004
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.9 | 21.8
|  | (Q) | 0.885 | 0.885 |  | 0.886 | 0.885
D1 & D2 |  | (L) | 43.8 | mH |  | 43.8 | mH
|  | (Q) | 0.889 |  |  | 0.889
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.89
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.08 | 3.08 |  | 3.08 | 3.07
D1 & D2 |  | (L) | 41.1 | mH |  | 41.1 | mH
|  | (Q) | 3.08 |  |  | 3.08
Magnet |  |  | (L) | 82.3 | mH
|  |  | (Q) | 3.09
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.2 | 6.09 |  | 6.71 | 6.8
|  | (Q) | 0.656 | 0.649 |  | 0.738 | 0.777
D1 & D2 |  | (L) | 12.3 | mH |  | 13.5 | mH
|  | (Q) | 0.649 |  |  | 0.753
Magnet |  |  | (L) | 25.8 | mH
|  |  | (Q) | 0.701
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000117 |  |  |  |  | Date: | 30/03/2004
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 15 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 17 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 4.84 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 4.46 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 10.1 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 11 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.952 | 0.954 |  | 0.952 | 0.956
| Dipoles D1 & D2 [4KV] |  | 1.76 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.64 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000117 |  |  |  |  | Date: | 30/03/2004
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.0223 | 22.1604 |  |  | 21.7675 | 22.1278
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.4888 | 22.5376 |  |  | 22.2635 | 22.6073
Insulation Resistance
QHs -----> Masse |  | 4.56 |  | GW |  | 4.66 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 4.02 |  | GW |  | 3.64 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 13.5 | 14.1 | GW |  | 12.5 | 11.3 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 38.7 | 149 |  | YT 211 | 37.9 | 148
| YT 112 | 38.9 | 153 |  | YT 212 | 37.5 | 151
| YT 121 | 37 | 152 |  | YT 221 | 37.6 | 150
| YT 122 | 37.5 | 149 |  | YT 222 | 36.5 | 153
Insulation Resistance
QHs -----> Masse |  | 6.7 |  | GW |  | 6.4 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 4.54 |  | GW |  | 4.18 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 14 | 14.5 | GW |  | 12.7 | 11.5 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.99 | 22.07 |  |  | 21.77 | 22.11
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.46 | 22.54 |  |  | 22.27 | 22.6