## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 22.6789 | Magnet | 5.9762 | 5976.172 | 6012.2455 | 10 | 0.887 | 21.8 |  | 0.887 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.5162 | Aperture1 | 2.988 | 2988.03 | 3006.0664 | 100 | 3.09 | 20.6 |  | 3.09 | 20.5
[9 empty] | YT121 | 22.449 | Aperture2 | 2.9881 | 2988.127 | 3006.164 | 1000 | 0.665 | 6.27 |  | 0.747 | 6.76
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 22.6608 | Apt1 Pup | 1.4947 | 1494.726 | 1503.7485
CERN PART NUMBER : |  |  | HCMBBL_A00101 |  | Serial Number : |  | 000120 |  | YT211 | 22.6339 | Apt1 Plw | 1.4933 | 1493.291 | 1502.3048 | 10 | 0.886 | 21.8 |  | 0.886 | 21.8
[9 empty] | YT212 | 22.0413 | Apt2 Pup | 1.4943 | 1494.279 | 1503.2988 | 100 | 3.09 | 20.5 |  | 3.08 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 22.6026 | Apt2 Plw | 1.4938 | 1493.834 | 1502.8511 | 1000 | 0.652 | 6.17 |  | 0.788 | 6.86
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.0984
[15 empty] | 10 | 0.89 | 43.7 |  | 0.89 | 43.7
NAME OF TEST OPERATOR: |  |  | WENDEL | [11 empty] | 100 | 3.08 | 41.2 |  | 3.1 | 41
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.653 | 12.4 |  | 0.766 | 13.6
DATE OF TEST : |  |  | 15/04/2004 |  | TIME :
[15 empty] | 10 | 0.891 | 87.5
[15 empty] | 100 | 3.1 | 82.2
[15 empty] | 1000 | 0.709 | 26.1
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 18.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 36 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1494.726 | 1493.291 |  | 1494.279 | 1493.834
Poles [20°C] |  |  | 1503.7485 | 1502.3048 |  | 1503.2988 | 1502.8511
D1 & D2 |  |  | 3006.0664 | mW |  | 3006.164 | mW
Magnet |  |  |  | 6012.2455 | mW
|  | Poles Nr. | JP 478 | JP 481 |  | JP 479 | JP 480
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 22.6789 | 22.449 |  | 22.6339 | 22.6026
|  |  | 22.5162 | 22.6608 |  | 22.0413 | 22.0984
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 210 | nF |  | 220 | nF
D1 & D2 -----> Ground |  |  | 210 | nF |  | 210 | nF
Magnet -----> Ground |  |  |  | 340 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000120 |  |  |  |  | Date: | 15/04/2004
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.887 | 0.886 |  | 0.887 | 0.886
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.89 |  |  | 0.89
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.891
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.09 | 3.09 |  | 3.08 | 3.08
D1 & D2 |  | (L) | 41.2 | mH |  | 41 | mH
|  | (Q) | 3.08 |  |  | 3.1
Magnet |  |  | (L) | 82.2 | mH
|  |  | (Q) | 3.1
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.27 | 6.17 |  | 6.76 | 6.86
|  | (Q) | 0.665 | 0.652 |  | 0.747 | 0.788
D1 & D2 |  | (L) | 12.4 | mH |  | 13.6 | mH
|  | (Q) | 0.653 |  |  | 0.766
Magnet |  |  | (L) | 26.1 | mH
|  |  | (Q) | 0.709
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000120 |  |  |  |  | Date: | 15/04/2004
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 15.6 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 19.1 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 5.75 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 6.75 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 17.3 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 14 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.3 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.964 | 0.96 |  | 0.944 | 0.964
| Dipoles D1 & D2 [4KV] |  | 1.76 | mS |  | 1.77 | mS
| Magnet [4KV] |  |  | 2.64 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000120 |  |  |  |  | Date: | 15/04/2004
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.6789 | 22.449 |  |  | 22.6339 | 22.6026
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.5162 | 22.6608 |  |  | 22.0413 | 22.0984
Insulation Resistance
QHs -----> Masse |  | 5.4 |  | GW |  | 5.75 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 4.5 |  | GW |  | 5.15 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 15.5 | 15.1 | GW |  | 15.9 | 15.8 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 36.7 | 153 |  | YT 211 | 36.7 | 153
| YT 112 | 36.6 | 152 |  | YT 212 | 37.3 | 149
| YT 121 | 37.1 | 152 |  | YT 221 | 36.7 | 153
| YT 122 | 36.2 | 153 |  | YT 222 | 37.4 | 150
Insulation Resistance
QHs -----> Masse |  | 7.8 |  | GW |  | 10.3 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 6 |  | GW |  | 5.2 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 14.9 | 14.4 | GW |  | 17.6 | 15.9 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.64 | 22.45 |  |  | 22.61 | 22.6
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.42 | 22.66 |  |  | 22.03 | 22.08
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION