## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 22.4083 | Magnet | 5.9863 | 5986.316 | 6046.7838 | 10 | 0.89 | 21.8 |  | 0.889 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.5885 | Aperture1 | 2.9929 | 2992.897 | 3023.1283 | 100 | 3.09 | 20.6 |  | 3.09 | 20.5
[9 empty] | YT121 | 22.3005 | Aperture2 | 2.9934 | 2993.387 | 3023.6232 | 1000 | 0.665 | 6.31 |  | 0.746 | 6.75
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 22.5437 | Apt1 Pup | 1.497 | 1497.002 | 1512.1232
CERN PART NUMBER : |  |  | HCMBBL_A00101 |  | Serial Number : |  | 000121 |  | YT211 | 22.4781 | Apt1 Plw | 1.4959 | 1495.851 | 1510.9606 | 10 | 0.888 | 21.8 |  | 0.889 | 21.8
[9 empty] | YT212 | 22.6325 | Apt2 Pup | 1.4979 | 1497.904 | 1513.0343 | 100 | 3.09 | 20.5 |  | 3.08 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 22.398 | Apt2 Plw | 1.4955 | 1495.458 | 1510.5636 | 1000 | 0.654 | 6.18 |  | 0.783 | 6.83
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.6898
[15 empty] | 10 | 0.893 | 43.7 |  | 0.893 | 43.8
NAME OF TEST OPERATOR: |  |  | JARDOT/GUTOWSKI/WENDEL | [11 empty] | 100 | 3.09 | 41.1 |  | 3.1 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.651 | 12.4 |  | 0.76 | 13.6
DATE OF TEST : |  |  | 20/04/2004 |  | TIME :
[15 empty] | 10 | 0.894 | 87.5
[15 empty] | 100 | 3.11 | 82.1
[15 empty] | 1000 | 0.704 | 26
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 17.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 38 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1497.002 | 1495.851 |  | 1497.904 | 1495.458
Poles [20°C] |  |  | 1512.1232 | 1510.9606 |  | 1513.0343 | 1510.5636
D1 & D2 |  |  | 3023.1283 | mW |  | 3023.6232 | mW
Magnet |  |  |  | 6046.7838 | mW
|  | Poles Nr. | JP 482 | JP 483 |  | JP 484 | JP 485
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 22.4083 | 22.3005 |  | 22.4781 | 22.398
|  |  | 22.5885 | 22.5437 |  | 22.6325 | 22.6898
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 220 | nF |  | 220 | nF
D1 & D2 -----> Ground |  |  | 210 | nF |  | 210 | nF
Magnet -----> Ground |  |  |  | 350 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000121 |  |  |  |  | Date: | 20/04/2004
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.89 | 0.888 |  | 0.889 | 0.889
D1 & D2 |  | (L) | 43.7 | mH |  | 43.8 | mH
|  | (Q) | 0.893 |  |  | 0.893
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.894
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.09 | 3.09 |  | 3.09 | 3.08
D1 & D2 |  | (L) | 41.1 | mH |  | 41.1 | mH
|  | (Q) | 3.09 |  |  | 3.1
Magnet |  |  | (L) | 82.1 | mH
|  |  | (Q) | 3.11
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.31 | 6.18 |  | 6.75 | 6.83
|  | (Q) | 0.665 | 0.654 |  | 0.746 | 0.783
D1 & D2 |  | (L) | 12.4 | mH |  | 13.6 | mH
|  | (Q) | 0.651 |  |  | 0.76
Magnet |  |  | (L) | 26 | mH
|  |  | (Q) | 0.704
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000121 |  |  |  |  | Date: | 20/04/2004
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 18.2 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 16.8 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 5.35 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 4.74 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 13.7 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 12 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.2 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.956 | 0.95 |  | 0.95 | 0.95
| Dipoles D1 & D2 [4KV] |  | 1.75 | mS |  | 1.77 | mS
| Magnet [4KV] |  |  | 2.64 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000121 |  |  |  |  | Date: | 20/04/2004
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.4083 | 22.3005 |  |  | 22.4781 | 22.398
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.5885 | 22.5437 |  |  | 22.6325 | 22.6898
Insulation Resistance
QHs -----> Masse |  | 7.35 |  | GW |  | 9.7 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 4.9 |  | GW |  | 3.6 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 14.3 | 14.6 | GW |  | 12.8 | 13.2 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 37.1 | 151 |  | YT 211 | 36.9 | 152
| YT 112 | 36.9 | 153 |  | YT 212 | 36.7 | 153
| YT 121 | 37.3 | 151 |  | YT 221 | 37.1 | 152
| YT 122 | 37 | 153 |  | YT 222 | 36.7 | 153
Insulation Resistance
QHs -----> Masse |  | 7.2 |  | GW |  | 10.8 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 5.65 |  | GW |  | 5.25 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 14.3 | 14.7 | GW |  | 13.2 | 13.5 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.41 | 22.33 |  |  | 22.49 | 22.41
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.62 | 22.57 |  |  | 22.65 | 22.67
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION