## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.942 | Magnet | 6.0744 | 6074.374 | 5990.5069 | 10 | 0.866 | 21.8 |  | 0.867 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 21.6647 | Aperture1 | 3.032 | 3031.995 | 2990.1331 | 100 | 3.05 | 20.6 |  | 3.08 | 20.5
[9 empty] | YT121 | 22.3062 | Aperture2 | 3.0424 | 3042.384 | 3000.3787 | 1000 | 0.661 | 6.21 |  | 0.745 | 6.78
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.8984 | Apt1 Pup | 1.5171 | 1517.074 | 1496.1282
CERN PART NUMBER : |  |  | HCMBBL_A00101 |  | Serial Number : |  | 000147 |  | YT211 | 21.9925 | Apt1 Plw | 1.5149 | 1514.923 | 1494.0069 | 10 | 0.867 | 21.8 |  | 0.866 | 21.8
[9 empty] | YT212 | 21.6362 | Apt2 Pup | 1.5253 | 1525.283 | 1504.2239 | 100 | 3.05 | 20.5 |  | 3.07 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 21.9549 | Apt2 Plw | 1.5171 | 1517.089 | 1496.143 | 1000 | 0.652 | 6.12 |  | 0.783 | 6.82
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.6055
[15 empty] | 10 | 0.87 | 43.7 |  | 0.87 | 43.7
NAME OF TEST OPERATOR: |  |  | WENDEL | [11 empty] | 100 | 3.05 | 41.1 |  | 3.08 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.651 | 12.3 |  | 0.761 | 13.5
DATE OF TEST : |  |  | 19/7/2004 |  | TIME :
[15 empty] | 10 | 0.869 | 87.5
[15 empty] | 100 | 3.07 | 82.2
[15 empty] | 1000 | 0.702 | 25.9
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 23.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 56.2 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1517.074 | 1514.923 |  | 1525.283 | 1517.089
Poles [20°C] |  |  | 1496.1282 | 1494.0069 |  | 1504.2239 | 1496.143
D1 & D2 |  |  | 2990.1331 | mW |  | 3000.3787 | mW
Magnet |  |  |  | 5990.5069 | mW
|  | Poles Nr. | JP586 | JP587 |  | JP588 | JP 589
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.942 | 22.3062 |  | 21.9925 | 21.9549
|  |  | 21.6647 | 21.8984 |  | 21.6362 | 21.6055
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 220 | nF |  | 220 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 220 | nF
Magnet -----> Ground |  |  |  | 340 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000147 |  |  |  |  | Date: | 19/7/2004
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.866 | 0.867 |  | 0.867 | 0.866
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.87 |  |  | 0.87
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.869
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.05 | 3.05 |  | 3.05 | 3.07
D1 & D2 |  | (L) | 41.1 | mH |  | 41.1 | mH
|  | (Q) | 3.05 |  |  | 3.08
Magnet |  |  | (L) | 82.2 | mH
|  |  | (Q) | 3.07
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.21 | 6.12 |  | 6.78 | 6.82
|  | (Q) | 0.661 | 0.652 |  | 0.745 | 0.783
D1 & D2 |  | (L) | 12.3 | mH |  | 13.5 | mH
|  | (Q) | 0.651 |  |  | 0.761
Magnet |  |  | (L) | 25.9 | mH
|  |  | (Q) | 0.702
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000147 |  |  |  |  | Date: | 19/7/2004
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 8.65 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 10.1 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 2.7 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 2.2 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 5.3 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 4.88 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.6 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.956 | 0.954 |  | 0.96 | 0.958
Verification absence court-circuit entre spires sur chaque pole (comparaison entre chocs 1KV et 4KV)
|  |  | OK | OK |  | OK | OK
| Dipoles D1 & D2 [4KV] |  | 1.76 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.64 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000147 |  |  |  |  | Date: | 19/7/2004
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.942 | 22.3062 |  |  | 21.9925 | 21.9549
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 21.6647 | 21.8984 |  |  | 21.6362 | 21.6055
Insulation Resistance
QHs -----> Masse |  | 3.34 |  | GW |  | 4.78 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 2.18 |  | GW |  | 2.34 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 5.7 | 6.75 | GW |  | 6.1 | 6 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 37.5 | 150 |  | YT 211 | 38.1 | 149
| YT 112 | 38.3 | 147 |  | YT 212 | 38.5 | 147
| YT 121 | 37.1 | 152 |  | YT 221 | 37.6 | 150
| YT 122 | 38 | 149 |  | YT 222 | 38.2 | 148
Insulation Resistance
QHs -----> Masse |  | 4.02 |  | GW |  | 4.6 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 2.06 |  | GW |  | 2.16 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 5.3 | 6.9 | GW |  | 6.3 | 6.2 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.94 | 22.3 |  |  | 21.98 | 21.97
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 21.6 | 21.92 |  |  | 21.63 | 21.61
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION