## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 22.2548 | Magnet | 6.0908 | 6090.759 | 6042.4196 | 10 | 0.869 | 21.8 |  | 0.87 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 21.8739 | Aperture1 | 3.047 | 3047.025 | 3022.8423 | 100 | 3.06 | 20.6 |  | 3.08 | 20.6
[9 empty] | YT121 | 22.5918 | Aperture2 | 3.0437 | 3043.724 | 3019.5675 | 1000 | 0.662 | 6.23 |  | 0.749 | 6.77
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 22.0552 | Apt1 Pup | 1.5261 | 1526.051 | 1513.9395
CERN PART NUMBER : |  |  | HCMBBL_A00101 |  | Serial Number : |  | 000148 |  | YT211 | 21.9108 | Apt1 Plw | 1.521 | 1520.962 | 1508.8909 | 10 | 0.869 | 21.8 |  | 0.87 | 21.8
[9 empty] | YT212 | 21.5656 | Apt2 Pup | 1.5221 | 1522.051 | 1509.9712 | 100 | 3.06 | 20.5 |  | 3.06 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 22.2727 | Apt2 Plw | 1.5217 | 1521.66 | 1509.5833 | 1000 | 0.653 | 6.14 |  | 0.784 | 6.81
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.9233
[15 empty] | 10 | 0.872 | 43.7 |  | 0.873 | 43.8
NAME OF TEST OPERATOR: |  |  | WENDEL/JARDOT | [11 empty] | 100 | 3.06 | 41.1 |  | 3.08 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.653 | 12.3 |  | 0.756 | 13.5
DATE OF TEST : |  |  | 2004-07-07 |  | TIME :
[15 empty] | 10 | 0.873 | 87.5
[15 empty] | 100 | 3.08 | 82.3
[15 empty] | 1000 | 0.706 | 25.8
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 22 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 55.8 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1526.051 | 1520.962 |  | 1522.051 | 1521.66
Poles [20°C] |  |  | 1513.9395 | 1508.8909 |  | 1509.9712 | 1509.5833
D1 & D2 |  |  | 3022.8423 | mW |  | 3019.5675 | mW
Magnet |  |  |  | 6042.4196 | mW
|  | Poles Nr. | JP 590 | JP 591 |  | JP 592 | JP 593
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 22.2548 | 22.5918 |  | 21.9108 | 22.2727
|  |  | 21.8739 | 22.0552 |  | 21.5656 | 21.9233
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 210 | nF |  | 210 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 330 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000148 |  |  |  |  | Date: | 2004-07-07
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.869 | 0.869 |  | 0.87 | 0.87
D1 & D2 |  | (L) | 43.7 | mH |  | 43.8 | mH
|  | (Q) | 0.872 |  |  | 0.873
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.873
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.6 | 20.5
|  | (Q) | 3.06 | 3.06 |  | 3.06 | 3.06
D1 & D2 |  | (L) | 41.1 | mH |  | 41.1 | mH
|  | (Q) | 3.06 |  |  | 3.08
Magnet |  |  | (L) | 82.3 | mH
|  |  | (Q) | 3.08
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.23 | 6.14 |  | 6.77 | 6.81
|  | (Q) | 0.662 | 0.653 |  | 0.749 | 0.784
D1 & D2 |  | (L) | 12.3 | mH |  | 13.5 | mH
|  | (Q) | 0.653 |  |  | 0.756
Magnet |  |  | (L) | 25.8 | mH
|  |  | (Q) | 0.706
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000148 |  |  |  |  | Date: | 2004-07-07
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 16.4 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 14.6 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 4.96 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 3.66 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 9.5 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 8.2 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.3 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.952 | 0.95 |  | 0.95 | 0.954
Verification absence court-circuit entre spires sur chaque pole (comparaison entre chocs 1KV et 4KV)
|  |  | OK | OK |  | OK | OK
| Dipoles D1 & D2 [4KV] |  | 1.76 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.65 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000148 |  |  |  |  | Date: | 2004-07-07
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.2548 | 22.5918 |  |  | 21.9108 | 22.2727
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 21.8739 | 22.0552 |  |  | 21.5656 | 21.9233
Insulation Resistance
QHs -----> Masse |  | 3.5 |  | GW |  | 4.86 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 3.18 |  | GW |  | 2.7 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 9.35 | 8.9 | GW |  | 8.45 | 9.1 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 37.5 | 152 |  | YT 211 | 38 | 149
| YT 112 | 38.1 | 149 |  | YT 212 | 38.5 | 147
| YT 121 | 37 | 153 |  | YT 221 | 37.2 | 152
| YT 122 | 37.7 | 150 |  | YT 222 | 37.8 | 149
Insulation Resistance
QHs -----> Masse |  | 7.5 |  | GW |  | 5.05 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 3.12 |  | GW |  | 3.48 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 9.6 | 9.2 | GW |  | 8.45 | 9.15 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 22.26 | 22.6 |  |  | 21.9 | 22.26
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 21.85 | 22.05 |  |  | 22.27 | 21.91
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION