## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.3965 | Magnet | 6.0201 | 6020.106 | 5984.2008 | 10 | 0.883 | 21.9 |  | 0.883 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 20.8517 | Aperture1 | 3.0107 | 3010.709 | 2992.7525 | 100 | 3.08 | 20.6 |  | 3.08 | 20.6
[9 empty] | YT121 | 21.1402 | Aperture2 | 3.0094 | 3009.372 | 2991.4235 | 1000 | 0.669 | 6.24 |  | 0.755 | 6.8
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.2504 | Apt1 Pup | 1.5059 | 1505.852 | 1496.8708
CERN PART NUMBER : |  |  | HCMBBL_A00101 |  | Serial Number : |  | 000171 |  | YT211 | 21.252 | Apt1 Plw | 1.5048 | 1504.844 | 1495.8688 | 10 | 0.882 | 21.9 |  | 0.882 | 21.9
[9 empty] | YT212 | 21.7209 | Apt2 Pup | 1.5046 | 1504.559 | 1495.5855 | 100 | 3.08 | 20.6 |  | 3.07 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 21.2912 | Apt2 Plw | 1.5048 | 1504.807 | 1495.832 | 1000 | 0.651 | 6.07 |  | 0.785 | 6.82
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.9132
[15 empty] | 10 | 0.886 | 43.8 |  | 0.886 | 43.8
NAME OF TEST OPERATOR: |  |  | HENRY/WENDEL | [11 empty] | 100 | 3.08 | 41.2 |  | 3.09 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.652 | 12.3 |  | 0.766 | 13.6
DATE OF TEST : |  |  | 2004-06-10 |  | TIME :
BAIE 2 | [14 empty] | 10 | 0.887 | 87.6
[15 empty] | 100 | 3.09 | 82.3
[15 empty] | 1000 | 0.707 | 25.8
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 21.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 58 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1505.852 | 1504.844 |  | 1504.559 | 1504.807
Poles [20°C] |  |  | 1496.8708 | 1495.8688 |  | 1495.5855 | 1495.832
D1 & D2 |  |  | 2992.7525 | mW |  | 2991.4235 | mW
Magnet |  |  |  | 5984.2008 | mW
|  | Poles Nr. | JP 682 | JP 683 |  | JP 684 | JP 685
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.3965 | 21.1402 |  | 21.252 | 21.2912
|  |  | 20.8517 | 21.2504 |  | 21.7209 | 21.9132
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 210 | nF |  | 210 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 340 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000171 |  |  |  |  | Date: | 2004-06-10
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.9 |  | 21.9 | 21.9
|  | (Q) | 0.883 | 0.882 |  | 0.883 | 0.882
D1 & D2 |  | (L) | 43.8 | mH |  | 43.8 | mH
|  | (Q) | 0.886 |  |  | 0.886
Magnet |  |  | (L) | 87.6 | mH
|  |  | (Q) | 0.887
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.6 |  | 20.6 | 20.5
|  | (Q) | 3.08 | 3.08 |  | 3.08 | 3.07
D1 & D2 |  | (L) | 41.2 | mH |  | 41.1 | mH
|  | (Q) | 3.08 |  |  | 3.09
Magnet |  |  | (L) | 82.3 | mH
|  |  | (Q) | 3.09
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.24 | 6.07 |  | 6.8 | 6.82
|  | (Q) | 0.669 | 0.651 |  | 0.755 | 0.785
D1 & D2 |  | (L) | 12.3 | mH |  | 13.6 | mH
|  | (Q) | 0.652 |  |  | 0.766
Magnet |  |  | (L) | 25.8 | mH
|  |  | (Q) | 0.707
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000171 |  |  |  |  | Date: | 2004-06-10
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 11.1 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 10.9 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 4.26 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 4.04 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 9 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 8.85 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.964 | 0.958 |  | 0.954 | 0.962
Verification absence court-circuit entre spires sur chaque pole (comparaison entre chocs 1KV et 4KV)
|  |  | OK | OK |  | OK | OK
| Dipoles D1 & D2 [4KV] |  | 1.76 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.65 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000171 |  |  |  |  | Date: | 2004-06-10
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.3965 | 21.1402 |  |  | 21.252 | 21.2912
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 20.8517 | 21.2504 |  |  | 21.7209 | 21.9132
Insulation Resistance
QHs -----> Masse |  | 5.85 |  | GW |  | 5.7 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 3.2 |  | GW |  | 3.48 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 10.4 | 9.9 | GW |  | 9.55 | 10.5 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 38.8 | 146 |  | YT 211 | 39.2 | 145
| YT 112 | 39.7 | 142 |  | YT 212 | 38.3 | 148
| YT 121 | 39.2 | 144 |  | YT 221 | 39.2 | 145
| YT 122 | 38.6 | 145 |  | YT 222 | 37.8 | 149
Insulation Resistance
QHs -----> Masse |  | 5.65 |  | GW |  | 5.45 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 3.52 |  | GW |  | 4 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 10.7 | 10.2 | GW |  | 9.6 | 10.7 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.38 | 21.13 |  |  | 21.23 | 21.28
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 20.84 | 21.24 |  |  | 21.71 | 21.9
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION