## Coll.1097
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.8437 | Magnet | 5.9756 | 5975.611 | 5987.5862 | 10 | 0.885 | 21.8 |  | 0.886 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.3763 | Aperture1 | 2.9877 | 2987.725 | 2993.7124 | 100 | 3.06 | 20.5 |  | 3.07 | 20.5
[9 empty] | YT121 | 21.7017 | Aperture2 | 2.9879 | 2987.888 | 2993.8758 | 1000 | 0.657 | 6.13 |  | 0.74 | 6.68
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 22.2639 | Apt1 Pup | 1.4951 | 1495.111 | 1498.1072
CERN PART NUMBER : |  |  | HCMBAL_A00101 |  | Serial Number : |  | 000097 |  | YT211 | 21.8226 | Apt1 Plw | 1.4926 | 1492.612 | 1495.6032 | 10 | 0.886 | 21.8 |  | 0.885 | 21.8
[9 empty] | YT212 | 22.4564 | Apt2 Pup | 1.4951 | 1495.11 | 1498.1062 | 100 | 3.06 | 20.5 |  | 3.07 | 20.4
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 21.7436 | Apt2 Plw | 1.4928 | 1492.763 | 1495.7545 | 1000 | 0.641 | 6.01 |  | 0.782 | 6.79
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.4147
[15 empty] | 10 | 0.889 | 43.7 |  | 0.889 | 43.7
NAME OF TEST OPERATOR: |  |  | GUTOWSKI / JARDOT | [11 empty] | 100 | 3.06 | 41 |  | 3.08 | 41
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.645 | 12.1 |  | 0.756 | 13.5
DATE OF TEST : |  |  | 2004-02-06 |  | TIME :
[15 empty] | 10 | 0.888 | 87.4
[15 empty] | 100 | 3.08 | 82
[15 empty] | 1000 | 0.7 | 25.6
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 37 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1495.111 | 1492.612 |  | 1495.11 | 1492.763
Poles [20°C] |  |  | 1498.1072 | 1495.6032 |  | 1498.1062 | 1495.7545
D1 & D2 |  |  | 2993.7124 | mW |  | 2993.8758 | mW
Magnet |  |  |  | 5987.5862 | mW
|  | Poles Nr. | JP 386 | JP 387 |  | JP 388 | JP 389
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.8437 | 21.7017 |  | 21.8226 | 21.7436
|  |  | 22.3763 | 22.2639 |  | 22.4564 | 22.4147
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 200 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 320 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000097 |  |  |  |  | Date: | 2004-02-06
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.885 | 0.886 |  | 0.886 | 0.885
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.889 |  |  | 0.889
Magnet |  |  | (L) | 87.4 | mH
|  |  | (Q) | 0.888
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.5 | 20.5 |  | 20.5 | 20.4
|  | (Q) | 3.06 | 3.06 |  | 3.06 | 3.07
D1 & D2 |  | (L) | 41 | mH |  | 41 | mH
|  | (Q) | 3.06 |  |  | 3.08
Magnet |  |  | (L) | 82 | mH
|  |  | (Q) | 3.08
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.13 | 6.01 |  | 6.68 | 6.79
|  | (Q) | 0.657 | 0.641 |  | 0.74 | 0.782
D1 & D2 |  | (L) | 12.1 | mH |  | 13.5 | mH
|  | (Q) | 0.645 |  |  | 0.756
Magnet |  |  | (L) | 25.6 | mH
|  |  | (Q) | 0.7
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000097 |  |  |  |  | Date: | 2004-02-06
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 17 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 20 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 5.3 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 4.88 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 14 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 13.5 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.952 | 0.95 |  | 0.952 | 0.956
| Dipoles D1 & D2 [4KV] |  | 1.76 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.64 | mS
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000097 |  |  |  |  | Date: | 2004-02-06
DIQH TEST
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.8437 | 21.7017 |  |  | 21.8226 | 21.7436
|  | YT 112 | YT 122 |  |  | YT 212 | YT 222
|  | 22.3763 | 22.2639 |  |  | 22.4564 | 22.4147
Insulation Resistance
QHs -----> Masse |  | 4.72 |  | GW |  | 4.98 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 4.22 |  | GW |  | 4.96 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 13.4 | 13.5 | GW |  | 14.1 | 13.7 | GW
[V=3.0.KV, 30'']
Discharge 850 V 2.5 KJ
|  | I (A) | T (ms) |  |  | I (A) | T (ms)
| YT 111 | 38.1 | 154 |  | YT 211 | 37.9 | 155
| YT 112 | 37.8 | 152 |  | YT 212 | 37.4 | 152
| YT 121 | 38.3 | 154 |  | YT 221 | 38.2 | 148
| YT 122 | 37.4 | 151 |  | YT 222 | 37 | 152
Insulation Resistance
QHs -----> Masse |  | 6.9 |  | GW |  | 6.95 |  | GW
[V=3.0.KV, 1']
QHs -----> Poles |  | 4.46 |  | GW |  | 5.35 |  | GW
[V=3.0.KV, 1']
Strip -----> Strip |  | 13.8 | 13.5 | GW |  | 14.2 | 13.7 | GW
[V=3.0.KV, 30'']
Resistance [W]
|  | YT 111 | YT 121 |  |  | YT 211 | YT 221
|  | 21.82 | 21.7 |  |  | 21.82 | 21.75
|  | YT 112 | YT 122 |  |  | YT212 | YT 222
|  | 22.36 | 22.27 |  |  | 22.46 | 22.41