## Coils-Coll.
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 20.5874 | Magnet | 6.0818 | 6081.797 | 6076.9355 | 10 | 0.874 | 21.7 |  | 0.874 | 21.7
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 20.5736 | Aperture1 | 3.0404 | 3040.426 | 3037.9956 | 100 | 2.21 | 18.9 |  | 2.21 | 18.9
[9 empty] | YT121 | 20.4611 | Aperture2 | 3.0414 | 3041.354 | 3041.354 | 1000 | 0.717 | 4.5 |  | 0.718 | 4.51
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 20.7171 | Apt1 Pup | 1.5205 | 1520.475 | 1519.2596
CERN PART NUMBER : |  |  | HCMBB_A001 |  | Serial Number : |  | 000003 |  | YT211 | 20.7192 | Apt1 Plw | 1.5199 | 1519.945 | 1518.73 | 10 | 0.874 | 21.7 |  | 0.874 | 21.7
[9 empty] | YT212 | 20.478 | Apt2 Pup | 1.5233 | 1523.304 | 1522.0863 | 100 | 2.21 | 18.9 |  | 2.21 | 18.9
CERN INSPECTION & TEST PLAN NUMBER : 16 To 24 |  |  |  |  | TEST NUMBER : |  | 16 to 24 |  | YT221 | 20.1936 | Apt2 Plw | 1.518 | 1518.041 | 1516.8275 | 1000 | 0.729 | 4.51 |  | 0.731 | 4.52
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.3527
[15 empty] | 10 | 0.878 | 43.4 |  | 0.878 | 43.4
NAME OF TEST OPERATOR: |  |  | c.mougenot | [11 empty] | 100 | 2.21 | 37.8 |  | 2.21 | 37.8
NAME OF RESPONSIBLE: |  |  | M.Schweitzer | [11 empty] | 1000 | 0.719 | 8.99 |  | 0.722 | 9.01
DATE OF TEST : |  |  | 2001-03-26 |  | TIME : |  | 15:30
[15 empty] | 10 | 0.877 | 86.7
[15 empty] | 100 | 2.21 | 75.5
[15 empty] | 1000 | 0.72 | 18
R[dc] of the Poles
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 20.2 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 35.3 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1520.475 | 1519.945 |  | 1523.304 | 1518.041
Poles [20°C] |  | * | 1519.2596 | 1518.73 |  | 1522.0863 | 1516.8275
D1 & D2 |  | * | 3037.9956 | mW |  | 3041.354 | mW
Magnet |  |  | * | 6076.9355 | mW
R[dc] of the Quench Heaters
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 20.5874 | 20.4611 |  | 20.7192 | 20.478
|  | * | 20.5736 | 20.7171 |  | 20.478 | 20.1936
Capacitance
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 210 | nF |  | 210 | nF
D1 & D2 | --> Masse |  | 210 | nF |  | 210 | nF
Magnet | --> Masse |  | * | 400 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.7 | 21.7 |  | 21.7 | 21.7
|  | (Q) | 0.874 | 0.874 |  | 0.874 | 0.874
D1 & D2 |  | (L) | 43.4 | mH |  | 43.4 | mH
|  | (Q) | 0.878 |  |  | 0.878
Magnet |  |  | (L) | 86.7 | mH
|  |  | (Q) | 0.877
INDUCTANCE L/Q[100Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 18.9 | 18.9 |  | 18.9 | 18.9
|  | (Q) | 2.21 | 2.21 |  | S16 | 2.21
D1 & D2 | * | (L) | 37.8 | mH |  | 37.8 | mH
|  | (Q) | 2.21 |  |  | 2.21
Magnet | * |  | (L) | 75.5 | mH
|  |  | (Q) | 2.21
INDUCTANCE L/Q[1.0KHz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 4.5 | 4.51 |  | 4.51 | 4.52
|  | (Q) | 0.717 | 0.729 |  | 0.718 | 0.731
D1 & D2 | * | (L) | 8.99 | mH |  | 9.01 | mH
|  | (Q) | 0.719 |  |  | 0.722
Magnet | * |  | (L) | 18 | mH
|  |  | (Q) | 0.72
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 7.8 | GW |  | >1000MW
[V=1.0.KV, 30'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 9 | GW |  | >1000MW
[V=1.0.KV, 30'']
| QHs D1(8x) D1 |  | * | 2.4 | GW |  | >1000MW
[V=1.0.KV, 30'']
| QHs D2(8x) D2 |  | * | 2.7 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 10 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 8 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.25 | µA
[V=5.0KV 4' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.2 | µA
[V=5.0KV 4' ]
| QHs D1(8x) D1 |  | * | 0.6 | µA
[V=3.0.KV 4' ]
| QHs D2(8x) D2 |  | * | 0.7 | µA
[V=3.0.KV 3' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.085 | µA
[V=3.KV 3']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.1 | µA
[V= 3KV 3']
DISCHARGE TEST
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 831.2 | 829.6 |  | 827.2 | 828
| Dipoles D1 & D2 [4KV] * |  | 1.72 | mS | * | 1.72 | mS
| Magnet [4KV] |  | * | 2.6 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1.600KV] |  | 296 | 284 | µS | 290 | 294 | µS
| [C= 2µF] | Current | 32 | 34.5 | A | 35.5 | 35 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION