## Coils-Coll.
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 20.5109 | Magnet | 6.0018 | 6001.84 | 6001.84 | 10 | 0.873 | 21.8 |  | 0.873 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 20.4569 | Aperture1 | 3.0014 | 3001.39 | 3001.39 | 100 | 2.19 | 19 |  | 2.2 | 19
[9 empty] | YT121 | 20.5122 | Aperture2 | 3.0005 | 3000.454 | 3000.454 | 1000 | 0.661 | 4.36 |  | 0.688 | 4.44
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 20.4685 | Apt1 Pup | 1.5002 | 1500.226 | 1500.226
CERN PART NUMBER : |  |  | HCMB__A001 |  | Serial Number : |  | 000004 |  | YT211 | 20.4073 | Apt1 Plw | 1.5012 | 1501.162 | 1501.162 | 10 | 0.872 | 21.8 |  | 0.872 | 21.8
[9 empty] | YT212 | 20.3752 | Apt2 Pup | 1.4994 | 1499.416 | 1499.416 | 100 | 2.19 | 18.9 |  | 2.19 | 18.9
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 16 to 18 |  | TEST NUMBER : |  | 16 to 18 |  | YT221 | 20.7245 | Apt2 Plw | 1.501 | 1501.03 | 1501.03 | 1000 | 0.67 | 4.36 |  | 0.708 | 4.47
NON CONFORMITY: |  |  | Yes |  | NON CONFORMITY: |  | Number |  | YT222 | 20.7014
[15 empty] | 10 | 0.873 | 43.6 |  | 0.873 | 43.6
NAME OF TEST OPERATOR: |  |  | M.Schweitzer | [11 empty] | 100 | 2.19 | 37.8 |  | 2.2 | 37.9
NAME OF RESPONSIBLE: |  |  | M.Schweitzer | [11 empty] | 1000 | 0.664 | 8.69 |  | 0.701 | 8.97
DATE OF TEST : |  |  | 2001-05-23 |  | TIME : |  | 9
[15 empty] | 10 | 0.873 | 87.2
[15 empty] | 100 | 2.2 | 75.8
[15 empty] | 1000 | 0.68 | 17.6
R[dc] of the Poles
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 20 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 44 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1500.226 | 1501.162 |  | 1499.416 | 1501.03
Poles [20°C] |  | * | 1500.226 | 1501.162 |  | 1499.416 | 1501.03
D1 & D2 |  | * | 3001.39 | mW |  | 3000.454 | mW
Magnet |  |  | * | 6001.84 | mW
|  | Poles Nr. | JP13 | JP15 |  | JP14 | JP16
R[dc] of the Quench Heaters
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 20.5109 | 20.5122 |  | 20.4073 | 20.3752
|  | * | 20.4569 | 20.4685 |  | 20.3752 | 20.7245
Capacitance
[ Megger 200V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 220 | nF |  | 220 | nF
D1 & D2 | --> Masse |  | 220 | nF |  | 220 | nF
Magnet | --> Masse |  | * | 360 | nF
ELECTRICAL TESTS OF DIPOLES
|  | AFTER COLLARING |  |  |  | Date: | 2001-05-23
(WITH BEAM TUBE)
Serial Nr. | 000004
INDUCTANCE L/Q[10Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.873 | 0.872 |  | 0.873 | 0.872
D1 & D2 |  | (L) | 43.6 | mH |  | 43.6 | mH
|  | (Q) | 0.873 |  |  | 0.873
Magnet |  |  | (L) | 87.2 | mH
|  |  | (Q) | 0.873
INDUCTANCE L/Q[100Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 19 | 18.9 |  | 19 | 18.9
|  | (Q) | 2.19 | 2.19 |  | S16 | 2.19
D1 & D2 | * | (L) | 37.8 | mH |  | 37.9 | mH
|  | (Q) | 2.19 |  |  | 2.2
Magnet | * |  | (L) | 75.8 | mH
|  |  | (Q) | 2.2
INDUCTANCE L/Q[1.0KHz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 4.36 | 4.36 |  | 4.44 | 4.47
|  | (Q) | 0.661 | 0.67 |  | 0.688 | 0.708
D1 & D2 | * | (L) | 8.69 | mH |  | 8.97 | mH
|  | (Q) | 0.664 |  |  | 0.701
Magnet | * |  | (L) | 17.6 | mH
|  |  | (Q) | 0.68
ELECTRICAL TESTS OF DIPOLES
|  | AFTER COLLARING |  |  |  | Date : | 2001-05-23
(WITH BEAM TUBE)
Serial Nr. | 000004
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 10.1 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 ----> Masse *
|  |  |  | 9.55 | GW |  | >1000MW
[V=1.0.KV, 1'']
| QHs D1(8x) D1 |  | *
|  |  |  | 2.54 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) D2 |  | *
|  |  |  | 2.46 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 9.35 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 8.85 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.1 | µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.2 | µA
[V=6.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.1 | µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.1 | µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.5 | µA
[V=3.KV 5']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.6 | µA
[V= 3KV 5']
DISCHARGE TEST
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.874 | 0.872 |  | 0.866 | 0.872
| Dipoles D1 & D2 [4KV] * |  | 1.76 | mS | * | 1.74 | mS
| Magnet [4KV] |  | * | 2.66 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=800V] |  | 230 - 230 | 230 - 230 | µS | 230 - 230 | 230 - 230 | µS
|  | Current | 38.0 - 38.0 | 38.5 - 33.5 | A | 33.5 - 39.5 | 34.0 - 37.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION