## Coils-Coll.
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 20.7043 | Magnet | 5.9598 | 5959.816 | 5983.751 | 10 | 0.874 | 21.7 |  | 0.873 | 21.7
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 20.6101 | Aperture1 | 2.9809 | 2980.935 | 2992.9066 | 100 | 2.17 | 18.8 |  | 2.17 | 18.8
[9 empty] | YT121 | 20.7331 | Aperture2 | 2.9789 | 2978.887 | 2978.887 | 1000 | 0.645 | 4.16 |  | 0.668 | 4.23
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 20.3852 | Apt1 Pup | 1.4914 | 1491.424 | 1497.4137
CERN PART NUMBER : |  |  | HCMBB_A001 |  | Serial Number : |  | 000006 |  | YT211 | 20.4254 | Apt1 Plw | 1.4895 | 1489.51 | 1495.492 | 10 | 0.873 | 21.7 |  | 0.873 | 21.8
[9 empty] | YT212 | 20.3452 | Apt2 Pup | 1.4895 | 1489.456 | 1495.4378 | 100 | 2.16 | 18.7 |  | 2.17 | 18.8
CERN INSPECTION & TEST PLAN NUMBER : 9a To 9i |  |  |  |  | TEST NUMBER : |  | 9a to 9i |  | YT221 | 20.4361 | Apt2 Plw | 1.4894 | 1489.424 | 1495.4056 | 1000 | 0.648 | 4.13 |  | 0.692 | 4.28
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.2493
[15 empty] | 10 | 0.873 | 43.5 |  | 0.874 | 43.5
NAME OF TEST OPERATOR: |  |  | N.Henry | [11 empty] | 100 | 2.16 | 37.5 |  | 2.17 | 37.6
NAME OF RESPONSIBLE: |  |  | M.Schweitzer | [11 empty] | 1000 | 0.647 | 8.32 |  | 0.683 | 8.56
DATE OF TEST : |  |  | 10,11/09/2001 |  | TIME : |  | 9:00
[15 empty] | 10 | 0.878 | 87.1
[15 empty] | 100 | 2.17 | 75.2
[15 empty] | 1000 | 0.66 | 16.8
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 51 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1491.424 | 1489.51 |  | 1489.456 | 1489.424
Poles [20°C] |  | * | 1497.4137 | 1495.492 |  | 1495.4378 | 1495.4056
D1 & D2 |  | * | 2992.9066 | mW |  | 2978.887 | mW
Magnet |  |  | * | 5983.751 | mW
|  | Poles Nr. | JP21 | JP22 |  | JP23 | JP24
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 20.7043 | 20.7331 |  | 20.4254 | 20.3452
|  | * | 20.6101 | 20.3852 |  | 20.3452 | 20.4361
Capacitance |  |  | ITPstep 9d/e
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 220 | nF |  | 220 | nF
D1 & D2 | --> Masse |  | 220 | nF |  | 220 | nF
Magnet | --> Masse |  | * | 370 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
Serial Nr: | 000006 |  |  |  |  | Date: | 10,11/09/2001
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.7 | 21.7 |  | 21.7 | 21.8
|  | (Q) | 0.874 | 0.873 |  | 0.873 | 0.873
D1 & D2 |  | (L) | 43.5 | mH |  | 43.5 | mH
|  | (Q) | 0.873 |  |  | 0.874
Magnet |  |  | (L) | 87.1 | mH
|  |  | (Q) | 0.878
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 18.8 | 18.7 |  | 18.8 | 18.8
|  | (Q) | 2.17 | 2.16 |  | 2.16 | 2.17
D1 & D2 | * | (L) | 37.5 | mH |  | 37.6 | mH
|  | (Q) | 2.16 |  |  | 2.17
Magnet | * |  | (L) | 75.2 | mH
|  |  | (Q) | 2.17
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 4.16 | 4.13 |  | 4.23 | 4.28
|  | (Q) | 0.645 | 0.648 |  | 0.668 | 0.692
D1 & D2 | * | (L) | 8.32 | mH |  | 8.56 | mH
|  | (Q) | 0.647 |  |  | 0.683
Magnet | * |  | (L) | 16.8 | mH
|  |  | (Q) | 0.66
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
Serial Nr: | 000006 |  | (WITH BEAM TUBE) |  |  | Date: | 10,11/09/2001
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 12.5 | GW |  | >1000MW
[V=1.0.KV, 30'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 9.4 | GW |  | >1000MW
[V=1.0.KV, 30'']
| QHs D1(8x) D1 |  | * | 4.88 | GW |  | >1000MW
[V=1.0.KV, 30'']
| QHs D2(8x) D2 |  | * | 4.66 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 13.8 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 20.2 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f/h
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.2 | µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.2 | µA
[V=6.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.1 | µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.1 | µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.2 | µA
[V=3.KV 3']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.3 | µA
[V= 3KV 3']
DISCHARGE TEST |  |  | ITP step 9i
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.834 | 0.846 |  | 0.842 | 0.844
| Dipoles D1 & D2 [4KV] * |  | 1.73 | mS | * | 1.73 | mS
| Magnet [4KV] |  | * | 2.6 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 372 | 380 | µS | 360 | 378 | µS
| [C= 2µF] | Current | 35 | 37.5 | A | 41 | 30.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION