## Coils-Coll.
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 20.6602 | Magnet | 5.9242 | 5924.242 | 5972.0181 | 10 | 0.884 | 21.8 |  | 0.885 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 20.7065 | Aperture1 | 2.9574 | 2957.441 | 2981.2913 | 100 | 2.16 | 18.8 |  | 2.17 | 18.8
[9 empty] | YT121 | 20.5065 | Aperture2 | 2.9668 | 2966.797 | 2966.797 | 1000 | 0.645 | 4.14 |  | 0.679 | 4.28
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 20.5748 | Apt1 Pup | 1.4804 | 1480.404 | 1492.3427
CERN PART NUMBER : |  |  | HCMBB_A001 |  | Serial Number : |  | 000009 |  | YT211 | 20.6202 | Apt1 Plw | 1.477 | 1477.041 | 1488.9526 | 10 | 0.885 | 21.7 |  | 0.885 | 21.8
[9 empty] | YT212 | 20.9085 | Apt2 Pup | 1.4889 | 1488.945 | 1500.9526 | 100 | 2.16 | 18.7 |  | 2.17 | 18.8
CERN INSPECTION & TEST PLAN NUMBER : 9a To 9i |  |  |  |  | TEST NUMBER : |  | 9a to 9i |  | YT221 | 20.6239 | Apt2 Plw | 1.4778 | 1477.847 | 1489.7651 | 1000 | 0.656 | 4.17 |  | 0.699 | 4.3
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.5834
[15 empty] | 10 | 0.889 | 43.6 |  | 0.889 | 43.6
NAME OF TEST OPERATOR: |  |  | HENRY | [11 empty] | 100 | 2.17 | 37.6 |  | 2.18 | 37.7
NAME OF RESPONSIBLE: |  |  | M.Schweitzer | [11 empty] | 1000 | 0.651 | 8.31 |  | 0.686 | 8.55
DATE OF TEST : |  |  | 20,21/12/2001 |  | TIME : |  | 10:00
[15 empty] | 10 | 0.89 | 87.2
[15 empty] | 100 | 2.17 | 75.3
[15 empty] | 1000 | 0.666 | 16.9
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 18 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 28 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1480.404 | 1477.041 |  | 1488.945 | 1477.847
Poles [20°C] |  | * | 1492.3427 | 1488.9526 |  | 1500.9526 | 1489.7651
D1 & D2 |  | * | 2981.2913 | mW |  | 2966.797 | mW
Magnet |  |  | * | 5972.0181 | mW
|  | Poles Nr. | JP41 | JP42 |  | JP43 | JP44
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 20.6602 | 20.5065 |  | 20.6202 | 20.9085
|  | * | 20.7065 | 20.5748 |  | 20.9085 | 20.6239
Capacitance |  |  | ITPstep 9d/e
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 200 | nF |  | 200 | nF
D1 & D2 | --> Masse |  | 150 | nF |  | 150 | nF
Magnet | --> Masse |  | * | 300 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
Serial Nr: | 000009 |  |  |  |  | Date: | 20,21/12/2001
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.7 |  | 21.8 | 21.8
|  | (Q) | 0.884 | 0.885 |  | 0.885 | 0.885
D1 & D2 |  | (L) | 43.6 | mH |  | 43.6 | mH
|  | (Q) | 0.889 |  |  | 0.889
Magnet |  |  | (L) | 87.2 | mH
|  |  | (Q) | 0.89
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 18.8 | 18.7 |  | 18.8 | 18.8
|  | (Q) | 2.16 | 2.16 |  | 2.17 | 2.17
D1 & D2 | * | (L) | 37.6 | mH |  | 37.7 | mH
|  | (Q) | 2.17 |  |  | 2.18
Magnet | * |  | (L) | 75.3 | mH
|  |  | (Q) | 2.17
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 4.14 | 4.17 |  | 4.28 | 4.3
|  | (Q) | 0.645 | 0.656 |  | 0.679 | 0.699
D1 & D2 | * | (L) | 8.31 | mH |  | 8.55 | mH
|  | (Q) | 0.651 |  |  | 0.686
Magnet | * |  | (L) | 16.9 | mH
|  |  | (Q) | 0.666
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
Serial Nr: | 000009 |  | (WITH BEAM TUBE) |  |  | Date: | 20,21/12/2001
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 13.4 | GW |  | >1000MW
[V=1.0.KV, 30'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 15.8 | GW |  | >1000MW
[V=1.0.KV, 30'']
| QHs D1(8x) D1 |  | * | 6 | GW |  | >1000MW
[V=1.0.KV, 30'']
| QHs D2(8x) D2 |  | * | 7.15 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 17.1 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 22.2 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f/h
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 1.1 | µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.7 | µA
[V=6.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.1 | µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.1 | µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.3 | µA
[V=3.KV 3']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.3 | µA
[V= 3KV 3']
DISCHARGE TEST |  |  | ITP step 9i
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.83 | 0.876 |  | 0.824 | 0.852
| Dipoles D1 & D2 [4KV] * |  | 1.76 | mS | * | 1.79 | mS
| Magnet [4KV] |  | * | 2.62 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 350 | 347 | µS | 366 | 355 | µS
| [C= 2µF] | Current | 39.5 | 38.5 | A | 36.5 | 38 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION