## Coils-Coll.
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 21.1997 | Magnet | 6.0574 | 6057.379 | 5997.405 | 10 | 0.86 | 21.8 |  | 0.86 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 20.934 | Aperture1 | 3.0281 | 3028.071 | 2998.0901 | 100 | 2.21 | 19 |  | 2.2 | 18.9
[9 empty] | YT121 | 21.0009 | Aperture2 | 3.0293 | 3029.304 | 3029.304 | 1000 | 0.661 | 4.36 |  | 0.684 | 4.42
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.2659 | Apt1 Pup | 1.5146 | 1514.565 | 1499.5693
CERN PART NUMBER : |  |  | HCMBB_A00101 |  | Serial Number : |  | 000023 |  | YT211 | 20.707 | Apt1 Plw | 1.5135 | 1513.493 | 1498.5079 | 10 | 0.86 | 21.7 |  | 0.859 | 21.8
[9 empty] | YT212 | 21.0653 | Apt2 Pup | 1.5149 | 1514.934 | 1499.9347 | 100 | 2.2 | 18.9 |  | 2.2 | 18.9
CERN INSPECTION & TEST PLAN NUMBER : 9a To 9i |  |  |  |  | TEST NUMBER : |  | 9a to 9i |  | YT221 | 21.2033 | Apt2 Plw | 1.5144 | 1514.36 | 1499.3663 | 1000 | 0.66 | 4.32 |  | 0.709 | 4.45
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.7291
[15 empty] | 10 | 0.865 | 43.6 |  | 0.864 | 43.6
NAME OF TEST OPERATOR: |  |  | HENRY/JARDOT | [11 empty] | 100 | 2.2 | 38 |  | 2.2 | 37.8
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.66 | 8.71 |  | 0.692 | 8.83
DATE OF TEST : |  |  | 02,03/10/2002 |  | TIME : |  | 10:00
[15 empty] | 10 | 0.865 | 87.2
[15 empty] | 100 | 2.21 | 75.9
[15 empty] | 1000 | 0.675 | 17.5
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 22.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 41 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1514.565 | 1513.493 |  | 1514.934 | 1514.36
Poles [20°C] |  | * | 1499.5693 | 1498.5079 |  | 1499.9347 | 1499.3663
D1 & D2 |  | * | 2998.0901 | mW |  | 3029.304 | mW
Magnet |  |  | * | 5997.405 | mW
|  | Poles Nr. | JP 89 | JP 90 |  | JP 91 | JP 92
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 21.1997 | 21.0009 |  | 20.707 | 21.2033
|  | * | 20.934 | 21.2659 |  | 21.0653 | 21.7291
Capacitance |  |  | ITPstep 9d/e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 210 | nF |  | 210 | nF
D1 & D2 | --> Masse |  | 190 | nF |  | 190 | nF
Magnet | --> Masse |  | * | 310 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
Serial Nr: | 000023 |  |  |  |  | Date: | 02,03/10/2002
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.7 |  | 21.8 | 21.8
|  | (Q) | 0.86 | 0.86 |  | 0.86 | 0.859
D1 & D2 |  | (L) | 43.6 | mH |  | 43.6 | mH
|  | (Q) | 0.865 |  |  | 0.864
Magnet |  |  | (L) | 87.2 | mH
|  |  | (Q) | 0.865
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 19 | 18.9 |  | 18.9 | 18.9
|  | (Q) | 2.21 | 2.2 |  | 2.2 | 2.2
D1 & D2 | * | (L) | 38 | mH |  | 37.8 | mH
|  | (Q) | 2.2 |  |  | 2.2
Magnet | * |  | (L) | 75.9 | mH
|  |  | (Q) | 2.21
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 4.36 | 4.32 |  | 4.42 | 4.45
|  | (Q) | 0.661 | 0.66 |  | 0.684 | 0.709
D1 & D2 | * | (L) | 8.71 | mH |  | 8.83 | mH
|  | (Q) | 0.66 |  |  | 0.692
Magnet | * |  | (L) | 17.5 | mH
|  |  | (Q) | 0.675
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
Serial Nr: | 000023 |  | (WITH BEAM TUBE) |  |  | Date: | 02,03/10/2002
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 10.2 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 8.6 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) D1 |  | * | 2.52 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) D2 |  | * | 2.22 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 7.75 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 6.8 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f/h
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.1 | µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.1 | µA
[V=6.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.1 | µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.1 | µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.3 | µA
[V=3.KV 5']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.3 | µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.882 | 0.868 |  | 0.868 | 0.892
| Dipoles D1 & D2 [4KV] * |  | 1.76 | mS | * | 1.81 | mS
| Magnet [4KV] |  | * | 2.7 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 381 | 401 | µS | 396 | 397 | µS
| [C= 2µF] | Current | 36 | 37.5 | A | 41.5 | 37.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION