## Coils-Coll.
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 21.1139 | Magnet | 5.9579 | 5957.925 | 5974.654 | 10 | 0.877 | 21.8 |  | 0.875 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 20.5382 | Aperture1 | 2.9787 | 2978.656 | 2987.0197 | 100 | 2.22 | 19 |  | 2.22 | 18.9
[9 empty] | YT121 | 20.8331 | Aperture2 | 2.9793 | 2979.262 | 2979.262 | 1000 | 0.653 | 4.4 |  | 0.702 | 4.44
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 20.8861 | Apt1 Pup | 1.4901 | 1490.101 | 1494.285
CERN PART NUMBER : |  |  | HCMBB_A00101 |  | Serial Number : |  | 000024 |  | YT211 | 20.6777 | Apt1 Plw | 1.4885 | 1488.541 | 1492.7206 | 10 | 0.875 | 21.8 |  | 0.876 | 21.8
[9 empty] | YT212 | 20.5063 | Apt2 Pup | 1.4898 | 1489.833 | 1494.0162 | 100 | 2.21 | 18.9 |  | 2.22 | 19
CERN INSPECTION & TEST PLAN NUMBER : 9a To 9i |  |  |  |  | TEST NUMBER : |  | 9a to 9i |  | YT221 | 20.8619 | Apt2 Plw | 1.4894 | 1489.411 | 1493.5931 | 1000 | 0.659 | 4.3 |  | 0.681 | 4.4
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.4029
[15 empty] | 10 | 0.88 | 43.6 |  | 0.88 | 43.6
NAME OF TEST OPERATOR: |  |  | HENRY/JARDOT | [11 empty] | 100 | 2.22 | 38 |  | 2.22 | 37.9
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.654 | 8.59 |  | 0.687 | 8.8
DATE OF TEST : |  |  | 11,14/10/2002 |  | TIME : |  | 10:00
[15 empty] | 10 | 0.879 | 87.2
[15 empty] | 100 | 2.22 | 76
[15 empty] | 1000 | 0.666 | 17.3
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19.3 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 46.5 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1490.101 | 1488.541 |  | 1489.833 | 1489.411
Poles [20°C] |  | * | 1494.285 | 1492.7206 |  | 1494.0162 | 1493.5931
D1 & D2 |  | * | 2987.0197 | mW |  | 2979.262 | mW
Magnet |  |  | * | 5974.654 | mW
|  | Poles Nr. | JP 97 | JP 98 |  | JP 99 | JP 100
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 21.1139 | 20.8331 |  | 20.6777 | 20.8619
|  | * | 20.5382 | 20.8861 |  | 20.5063 | 20.4029
Capacitance |  |  | ITPstep 9d/e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 200 | nF |  | 200 | nF
D1 & D2 | --> Masse |  | 190 | nF |  | 190 | nF
Magnet | --> Masse |  | * | 310 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
Serial Nr: | 000024 |  |  |  |  | Date: | 11,14/10/2002
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.877 | 0.875 |  | 0.875 | 0.876
D1 & D2 |  | (L) | 43.6 | mH |  | 43.6 | mH
|  | (Q) | 0.88 |  |  | 0.88
Magnet |  |  | (L) | 87.2 | mH
|  |  | (Q) | 0.879
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 19 | 18.9 |  | 18.9 | 19
|  | (Q) | 2.22 | 2.21 |  | 2.22 | 2.22
D1 & D2 | * | (L) | 38 | mH |  | 37.9 | mH
|  | (Q) | 2.22 |  |  | 2.22
Magnet | * |  | (L) | 76 | mH
|  |  | (Q) | 2.22
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 4.4 | 4.3 |  | 4.44 | 4.4
|  | (Q) | 0.653 | 0.659 |  | 0.702 | 0.681
D1 & D2 | * | (L) | 8.59 | mH |  | 8.8 | mH
|  | (Q) | 0.654 |  |  | 0.687
Magnet | * |  | (L) | 17.3 | mH
|  |  | (Q) | 0.666
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
Serial Nr: | 000024 |  | (WITH BEAM TUBE) |  |  | Date: | 11,14/10/2002
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 11.9 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 10.2 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) D1 |  | * | 3.44 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) D2 |  | * | 2.82 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 11 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 9.6 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f/h
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.1 | µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.1 | µA
[V=6.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.3 | µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.35 | µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.06 | µA
[V=3.KV 5']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.08 | µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.88 | 0.886 |  | 0.886 | 0.888
| Dipoles D1 & D2 [4KV] * |  | 1.79 | mS | * | 1.77 | mS
| Magnet [4KV] |  | * | 2.7 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 398 | 418 | µS | 414 | 402 | µS
| [C= 2µF] | Current | 40 | 45 | A | 43.5 | 38.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION