## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 20.965 | Magnet | 5.8755 | 5875.538 | 5922.9214 | 10 | 0.894 | 21.8 |  | 0.89 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 20.7516 | Aperture1 | 2.9389 | 2938.944 | 2962.6452 | 100 | 2.23 | 19 |  | 2.23 | 19
[9 empty] | YT121 | 20.8881 | Aperture2 | 2.9366 | 2936.598 | 2936.598 | 1000 | 0.655 | 4.35 |  | 0.681 | 4.44
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 20.928 | Apt1 Pup | 1.4709 | 1470.922 | 1482.7843
CERN PART NUMBER : |  |  | HCMBB_A00101 |  | Serial Number : |  | 000027Bis |  | YT211 | 21.377 | Apt1 Plw | 1.468 | 1468.015 | 1479.8538 | 10 | 0.894 | 21.8 |  | 0.888 | 21.8
[9 empty] | YT212 | 21.1933 | Apt2 Pup | 1.4684 | 1468.404 | 1480.246 | 100 | 2.23 | 19 |  | 2.24 | 19
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.6568 | Apt2 Plw | 1.4682 | 1468.188 | 1480.0282 | 1000 | 0.66 | 4.34 |  | 0.704 | 4.48
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.7082
[15 empty] | 10 | 0.892 | 43.7 |  | 0.892 | 43.7
NAME OF TEST OPERATOR: |  |  | JARDOT | [11 empty] | 100 | 2.23 | 38.1 |  | 2.23 | 38
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.654 | 8.66 |  | 0.689 | 8.9
DATE OF TEST : |  |  | 28/01/2003 |  | TIME :
[15 empty] | 10 | 0.893 | 87.5
[15 empty] | 100 | 2.23 | 76.2
[15 empty] | 1000 | 0.67 | 17.5
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 18 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 41.5 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1470.922 | 1468.015 |  | 1468.404 | 1468.188
Poles [20°C] |  |  | 1482.7843 | 1479.8538 |  | 1480.246 | 1480.0282
D1 & D2 |  |  | 2962.6452 | mW |  | 2936.598 | mW
Magnet |  |  |  | 5922.9214 | mW
|  | Poles Nr. | JP 109 | JP 110 |  | JP 111 | JP 112
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 20.965 | 20.8881 |  | 21.377 | 20.6568
|  |  | 20.7516 | 20.928 |  | 21.1933 | 20.7082
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 210 | nF |  | 210 | nF
D1 & D2 -----> Ground |  |  | 210 | nF |  | 210 | nF
Magnet -----> Ground |  |  |  | 350 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000027Bis |  |  |  |  | Date: | 28/01/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.894 | 0.894 |  | 0.89 | 0.888
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.892 |  |  | 0.892
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.893
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 19 | 19 |  | 19 | 19
|  | (Q) | 2.23 | 2.23 |  | 2.23 | 2.24
D1 & D2 |  | (L) | 38.1 | mH |  | 38 | mH
|  | (Q) | 2.23 |  |  | 2.23
Magnet |  |  | (L) | 76.2 | mH
|  |  | (Q) | 2.23
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 4.35 | 4.34 |  | 4.44 | 4.48
|  | (Q) | 0.655 | 0.66 |  | 0.681 | 0.704
D1 & D2 |  | (L) | 8.66 | mH |  | 8.9 | mH
|  | (Q) | 0.654 |  |  | 0.689
Magnet |  |  | (L) | 17.5 | mH
|  |  | (Q) | 0.67
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000027Bis |  |  |  |  | Date: | 28/01/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 29.4 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 31.2 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 12.8 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 12.5 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 25.2 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 26.6 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.3 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.3 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.4 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.4 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.862 | 0.874 |  | 0.882 | 0.874
| Dipoles D1 & D2 [4KV] |  | 1.8 | mS |  | 1.82 | mS
| Magnet [4KV] |  |  | 2.71 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 395 | 386 | µS | 400 | 391 | µS
| [C= 2µF] | Current | 37 | 35.5 | A | 40 | 38.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION