## Coils-Coll.
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 20.8647 | Magnet | 6.0305 | 6030.53 | 6030.53 | 10 | 0.891 | 21.9 |  | 0.891 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 20.8037 | Aperture1 | 3.0153 | 3015.313 | 3015.313 | 100 | 3.12 | 20.6 |  | 3.14 | 20.6
[9 empty] | YT121 | 20.786 | Aperture2 | 3.0152 | 3015.22 | 3015.22 | 1000 | 0.759 | 7.13 |  | 0.8 | 7.27
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 20.965 | Apt1 Pup | 1.5084 | 1508.448 | 1508.448
CERN PART NUMBER : |  |  | HCMBB_A00101 |  | Serial Number : |  | 000027 |  | YT211 | 21.0393 | Apt1 Plw | 1.5069 | 1506.865 | 1506.865 | 10 | 0.891 | 21.8 |  | 0.891 | 21.9
[9 empty] | YT212 | 20.9302 | Apt2 Pup | 1.5074 | 1507.426 | 1507.426 | 100 | 3.11 | 20.5 |  | 3.13 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 21.57 | Apt2 Plw | 1.5078 | 1507.789 | 1507.789 | 1000 | 0.76 | 7.06 |  | 0.828 | 7.27
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.5892
[15 empty] | 10 | 0.894 | 43.7 |  | 0.894 | 43.8
NAME OF TEST OPERATOR: |  |  | HENRY | [11 empty] | 100 | 3.13 | 41.2 |  | 3.14 | 41.2
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.753 | 14.1 |  | 0.81 | 14.5
DATE OF TEST : |  |  | 28,29/10/2002 |  | TIME :
[15 empty] | 10 | 0.896 | 87.6
[15 empty] | 100 | 3.14 | 82.4
[15 empty] | 1000 | 0.781 | 28.7
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 20 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 36.5 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1508.448 | 1506.865 |  | 1507.426 | 1507.789
Poles [20°C] |  |  | 1508.448 | 1506.865 |  | 1507.426 | 1507.789
D1 & D2 |  |  | 3015.313 | mW |  | 3015.22 | mW
Magnet |  |  |  | 6030.53 | mW
|  | Poles Nr. | JP 109 | JP 110 |  | JP 111 | JP 112
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 20.8647 | 20.786 |  | 21.0393 | 21.57
|  |  | 20.8037 | 20.965 |  | 20.9302 | 21.5892
Capacitance |  |  | ITPstep 9d/e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 200 | nF |  | 200 | nF
D1 & D2 | --> Masse |  | 200 | nF |  | 200 | nF
Magnet | --> Masse |  |  | 330 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
Serial Nr: | 000027 |  |  |  |  | Date: | 28,29/10/2002
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.8 |  | 21.9 | 21.9
|  | (Q) | 0.891 | 0.891 |  | 0.891 | 0.891
D1 & D2 |  | (L) | 43.7 | mH |  | 43.8 | mH
|  | (Q) | 0.894 |  |  | 0.894
Magnet |  |  | (L) | 87.6 | mH
|  |  | (Q) | 0.896
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.6 | 20.5
|  | (Q) | 3.12 | 3.11 |  | 3.13 | 3.13
D1 & D2 |  | (L) | 41.2 | mH |  | 41.2 | mH
|  | (Q) | 3.13 |  |  | 3.14
Magnet |  |  | (L) | 82.4 | mH
|  |  | (Q) | 3.14
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 7.13 | 7.06 |  | 7.27 | 7.27
|  | (Q) | 0.759 | 0.76 |  | 0.8 | 0.828
D1 & D2 |  | (L) | 14.1 | mH |  | 14.5 | mH
|  | (Q) | 0.753 |  |  | 0.81
Magnet |  |  | (L) | 28.7 | mH
|  |  | (Q) | 0.781
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
Serial Nr: | 000027 |  | (WITH BEAM TUBE) |  |  | Date: | 28,29/10/2002
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse |  |  |  | 14.1 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 ----> Masse |  |  |  | 16.7 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) D1 |  |  | 3.88 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) D2 |  |  | 4.44 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 12.2 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP -----> POLE LW |  |  | 13.1 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f/h
Dipole D1 + QHs D1 ----> Masse |  |  |  | 0.1 | µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse |  |  |  | 0.1 | µA
[V=6.0KV 5' ]
| QHs D1(8x) D1 |  |  | 0.1 | µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  |  | 0.1 | µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.2 | µA
[V=3.KV 5']
DIPOLE 2
| POLE UP -----> POLE LW |  |  | 0.2 | µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.97 | 0.974 |  | 0.974 | 0.974
| Dipoles D1 & D2 [4KV] |  | 1.81 | mS | * | 1.8 | mS
| Magnet [4KV] |  |  | 2.7 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 400 | 424 | µS | 395 | 421 | µS
| [C= 2µF] | Current | 38.5 | 37.5 | A | 37.5 | 37 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION