## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 20.9393 | Magnet | 5.9268 | 5926.755 | 5950.5572 | 10 | 0.882 | 21.8 |  | 0.883 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 21.0155 | Aperture1 | 2.9659 | 2965.935 | 2977.8464 | 100 | 2.21 | 19 |  | 2.2 | 18.9
[9 empty] | YT121 | 21.5656 | Aperture2 | 2.9608 | 2960.821 | 2960.821 | 1000 | 0.651 | 4.3 |  | 0.676 | 4.35
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.4655 | Apt1 Pup | 1.4838 | 1483.753 | 1489.7118
CERN PART NUMBER : |  |  | HCMBB_A00101 |  | Serial Number : |  | 000030 |  | YT211 | 21.5172 | Apt1 Plw | 1.4822 | 1482.17 | 1488.1225 | 10 | 0.881 | 21.8 |  | 0.882 | 21.8
[9 empty] | YT212 | 21.1465 | Apt2 Pup | 1.4806 | 1480.632 | 1486.5783 | 100 | 2.2 | 18.9 |  | 2.2 | 18.9
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.1473 | Apt2 Plw | 1.4802 | 1480.168 | 1486.1124 | 1000 | 0.658 | 4.3 |  | 0.702 | 4.41
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.4491
[15 empty] | 10 | 0.885 | 43.7 |  | 0.885 | 43.7
NAME OF TEST OPERATOR: |  |  | HENRY/JARDOT | [11 empty] | 100 | 2.2 | 38 |  | 2.2 | 37.9
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.651 | 8.57 |  | 0.686 | 8.74
DATE OF TEST : |  |  | 18/11/2002 |  | TIME :
[15 empty] | 10 | 0.886 | 87.4
[15 empty] | 100 | 2.2 | 75.9
[15 empty] | 1000 | 0.668 | 17.3
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 49.5 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1483.753 | 1482.17 |  | 1480.632 | 1480.168
Poles [20°C] |  |  | 1489.7118 | 1488.1225 |  | 1486.5783 | 1486.1124
D1 & D2 |  |  | 2977.8464 | mW |  | 2960.821 | mW
Magnet |  |  |  | 5950.5572 | mW
|  | Poles Nr. | JP 129 | JP 130 |  | JP 131 | JP 132
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 20.9393 | 21.5656 |  | 21.5172 | 20.1473
|  |  | 21.0155 | 21.4655 |  | 21.1465 | 20.4491
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 200 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 320 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000030 |  |  |  |  | Date: | 18/11/2002
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.882 | 0.881 |  | 0.883 | 0.882
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.885 |  |  | 0.885
Magnet |  |  | (L) | 87.4 | mH
|  |  | (Q) | 0.886
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 19 | 18.9 |  | 18.9 | 18.9
|  | (Q) | 2.21 | 2.2 |  | 2.2 | 2.2
D1 & D2 |  | (L) | 38 | mH |  | 37.9 | mH
|  | (Q) | 2.2 |  |  | 2.2
Magnet |  |  | (L) | 75.9 | mH
|  |  | (Q) | 2.2
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 4.3 | 4.3 |  | 4.35 | 4.41
|  | (Q) | 0.651 | 0.658 |  | 0.676 | 0.702
D1 & D2 |  | (L) | 8.57 | mH |  | 8.74 | mH
|  | (Q) | 0.651 |  |  | 0.686
Magnet |  |  | (L) | 17.3 | mH
|  |  | (Q) | 0.668
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000030 |  |  |  |  | Date: | 18/11/2002
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 13.4 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 13.2 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 3.62 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 3.34 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 12.4 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 10.6 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.982 | 0.97 |  | 0.966 | 0.964
| Dipoles D1 & D2 [4KV] |  | 1.8 | mS |  | 1.78 | mS
| Magnet [4KV] |  |  | 2.7 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 387 | 393 | µS | 397 | 407 | µS
| [C= 2µF] | Current | 39 | 40 | A | 39 | 41 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION