## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 21.031 | Magnet | 5.9332 | 5933.176 | 5968.9899 | 10 | 0.884 | 21.8 |  | 0.884 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 21.1921 | Aperture1 | 2.9669 | 2966.924 | 2984.833 | 100 | 2.18 | 18.9 |  | 2.18 | 18.9
[9 empty] | YT121 | 20.6187 | Aperture2 | 2.9663 | 2966.257 | 2966.257 | 1000 | 0.658 | 4.26 |  | 0.684 | 4.37
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 20.5797 | Apt1 Pup | 1.4845 | 1484.496 | 1493.4567
CERN PART NUMBER : |  |  | HCMBB_A00101 |  | Serial Number : |  | 000032 |  | YT211 | 20.8817 | Apt1 Plw | 1.4824 | 1482.412 | 1491.3602 | 10 | 0.883 | 21.8 |  | 0.883 | 21.8
[9 empty] | YT212 | 20.7403 | Apt2 Pup | 1.4843 | 1484.292 | 1493.2515 | 100 | 2.17 | 18.8 |  | 2.18 | 18.8
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.7797 | Apt2 Plw | 1.4819 | 1481.946 | 1490.8913 | 1000 | 0.662 | 4.24 |  | 0.706 | 4.39
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.8612
[15 empty] | 10 | 0.887 | 43.7 |  | 0.886 | 43.7
NAME OF TEST OPERATOR: |  |  | JARDOT | [11 empty] | 100 | 2.18 | 37.8 |  | 2.19 | 37.8
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.656 | 8.47 |  | 0.692 | 8.74
DATE OF TEST : |  |  | 17/01/2003 |  | TIME :
[15 empty] | 10 | 0.886 | 87.4
[15 empty] | 100 | 2.18 | 75.6
[15 empty] | 1000 | 0.672 | 17.2
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 18.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 37.8 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1484.496 | 1482.412 |  | 1484.292 | 1481.946
Poles [20°C] |  |  | 1493.4567 | 1491.3602 |  | 1493.2515 | 1490.8913
D1 & D2 |  |  | 2984.833 | mW |  | 2966.257 | mW
Magnet |  |  |  | 5968.9899 | mW
|  | Poles Nr. | JP 125 | JP 126 |  | JP 127 | JP 128
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.031 | 20.6187 |  | 20.8817 | 20.7797
|  |  | 21.1921 | 20.5797 |  | 20.7403 | 20.8612
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 210 | nF |  | 210 | nF
D1 & D2 -----> Ground |  |  | 210 | nF |  | 210 | nF
Magnet -----> Ground |  |  |  | 350 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000032 |  |  |  |  | Date: | 17/01/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.9 | 21.8
|  | (Q) | 0.884 | 0.883 |  | 0.884 | 0.883
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.887 |  |  | 0.886
Magnet |  |  | (L) | 87.4 | mH
|  |  | (Q) | 0.886
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 18.9 | 18.8 |  | 18.9 | 18.8
|  | (Q) | 2.18 | 2.17 |  | 2.18 | 2.18
D1 & D2 |  | (L) | 37.8 | mH |  | 37.8 | mH
|  | (Q) | 2.18 |  |  | 2.19
Magnet |  |  | (L) | 75.6 | mH
|  |  | (Q) | 2.18
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 4.26 | 4.24 |  | 4.37 | 4.39
|  | (Q) | 0.658 | 0.662 |  | 0.684 | 0.706
D1 & D2 |  | (L) | 8.47 | mH |  | 8.74 | mH
|  | (Q) | 0.656 |  |  | 0.692
Magnet |  |  | (L) | 17.2 | mH
|  |  | (Q) | 0.672
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000032 |  |  |  |  | Date: | 17/01/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 29.6 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 28.2 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 12.2 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 11 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 27 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 25.8 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.09 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.09 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.02 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.02 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.854 | 0.876 |  | 0.87 | 0.87
| Dipoles D1 & D2 [4KV] |  | 1.79 | mS |  | 1.82 | mS
| Magnet [4KV] |  |  | 2.72 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 390 | 386 | µS | 411 | 393 | µS
| [C= 2µF] | Current | 37.5 | 40 | A | 36.5 | 38 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION