## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 21.1948 | Magnet | 6.0355 | 6035.477 | 6059.7159 | 10 | 0.881 | 21.8 |  | 0.88 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 21.122 | Aperture1 | 3.0158 | 3015.785 | 3027.8966 | 100 | 2.22 | 19 |  | 2.23 | 19
[9 empty] | YT121 | 21.2321 | Aperture2 | 3.0197 | 3019.687 | 3019.687 | 1000 | 0.666 | 4.39 |  | 0.693 | 4.5
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.1884 | Apt1 Pup | 1.5085 | 1508.548 | 1514.6064
CERN PART NUMBER : |  |  | HCMBB_A00101 |  | Serial Number : |  | 000034 |  | YT211 | 20.9687 | Apt1 Plw | 1.5072 | 1507.224 | 1513.2771 | 10 | 0.881 | 21.8 |  | 0.879 | 21.9
[9 empty] | YT212 | 21.3887 | Apt2 Pup | 1.5108 | 1510.801 | 1516.8685 | 100 | 2.22 | 19 |  | 2.23 | 19
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 21.016 | Apt2 Plw | 1.5089 | 1508.885 | 1514.9448 | 1000 | 0.672 | 4.39 |  | 0.712 | 4.52
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.1389
[15 empty] | 10 | 0.884 | 43.7 |  | 0.883 | 43.7
NAME OF TEST OPERATOR: |  |  | HENRY/JARDOT | [11 empty] | 100 | 2.22 | 38 |  | 2.23 | 38.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.662 | 8.72 |  | 0.705 | 9.02
DATE OF TEST : |  |  | 12/02/2003 |  | TIME :
[15 empty] | 10 | 0.885 | 87.5
[15 empty] | 100 | 2.23 | 76.2
[15 empty] | 1000 | 0.681 | 17.7
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 27 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1508.548 | 1507.224 |  | 1510.801 | 1508.885
Poles [20°C] |  |  | 1514.6064 | 1513.2771 |  | 1516.8685 | 1514.9448
D1 & D2 |  |  | 3027.8966 | mW |  | 3019.687 | mW
Magnet |  |  |  | 6059.7159 | mW
|  | Poles Nr. | JP 137 | JP 138 |  | JP 139 | JP 140
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.1948 | 21.2321 |  | 20.9687 | 21.016
|  |  | 21.122 | 21.1884 |  | 21.3887 | 21.1389
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 200 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 210 | nF |  | 210 | nF
Magnet -----> Ground |  |  |  | 340 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000034 |  |  |  |  | Date: | 12/02/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.9 | 21.9
|  | (Q) | 0.881 | 0.881 |  | 0.88 | 0.879
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.884 |  |  | 0.883
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.885
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 19 | 19 |  | 19 | 19
|  | (Q) | 2.22 | 2.22 |  | 2.22 | 2.23
D1 & D2 |  | (L) | 38 | mH |  | 38.1 | mH
|  | (Q) | 2.22 |  |  | 2.23
Magnet |  |  | (L) | 76.2 | mH
|  |  | (Q) | 2.23
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 4.39 | 4.39 |  | 4.5 | 4.52
|  | (Q) | 0.666 | 0.672 |  | 0.693 | 0.712
D1 & D2 |  | (L) | 8.72 | mH |  | 9.02 | mH
|  | (Q) | 0.662 |  |  | 0.705
Magnet |  |  | (L) | 17.7 | mH
|  |  | (Q) | 0.681
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000034 |  |  |  |  | Date: | 12/02/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 49.8 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 51.5 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 23 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 24.6 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 30 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 29.2 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.4 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.4 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.4 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.872 | 0.87 |  | 0.866 | 0.866
| Dipoles D1 & D2 [4KV] |  | 1.79 | mS |  | 1.79 | mS
| Magnet [4KV] |  |  | 2.69 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 394 | 394 | µS | 404 | 398 | µS
| [C= 2µF] | Current | 38 | 36.5 | A | 38.5 | 39.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION