## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 21.0291 | Magnet | 5.9622 | 5962.233 | 5986.1777 | 10 | 0.878 | 21.8 |  | 0.878 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 20.9805 | Aperture1 | 2.9813 | 2981.263 | 2993.2359 | 100 | 2.22 | 19 |  | 2.23 | 19
[9 empty] | YT121 | 20.789 | Aperture2 | 2.981 | 2980.963 | 2980.963 | 1000 | 0.67 | 4.41 |  | 0.695 | 4.51
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.095 | Apt1 Pup | 1.4921 | 1492.098 | 1498.0904
CERN PART NUMBER : |  |  | HCMBB_A00101 |  | Serial Number : |  | 000036 |  | YT211 | 20.8893 | Apt1 Plw | 1.4891 | 1489.148 | 1495.1285 | 10 | 0.878 | 21.8 |  | 0.878 | 21.8
[9 empty] | YT212 | 21.0019 | Apt2 Pup | 1.492 | 1492.017 | 1498.009 | 100 | 2.22 | 19 |  | 2.23 | 19
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.9612 | Apt2 Plw | 1.4889 | 1488.924 | 1494.9036 | 1000 | 0.671 | 4.39 |  | 0.715 | 4.54
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.043
[15 empty] | 10 | 0.881 | 43.7 |  | 0.881 | 43.7
NAME OF TEST OPERATOR: |  |  | HENRY/JARDOT | [11 empty] | 100 | 2.22 | 38.1 |  | 2.23 | 38.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.666 | 8.79 |  | 0.699 | 8.99
DATE OF TEST : |  |  | 05/03/2003 |  | TIME :
[15 empty] | 10 | 0.883 | 87.5
[15 empty] | 100 | 2.23 | 76.2
[15 empty] | 1000 | 0.681 | 17.8
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 43.5 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1492.098 | 1489.148 |  | 1492.017 | 1488.924
Poles [20°C] |  |  | 1498.0904 | 1495.1285 |  | 1498.009 | 1494.9036
D1 & D2 |  |  | 2993.2359 | mW |  | 2980.963 | mW
Magnet |  |  |  | 5986.1777 | mW
|  | Poles Nr. | JP 145 | JP 146 |  | JP 147 | JP 148
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.0291 | 20.789 |  | 20.8893 | 20.9612
|  |  | 20.9805 | 21.095 |  | 21.0019 | 21.043
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 200 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 190 | nF |  | 190 | nF
Magnet -----> Ground |  |  |  | 310 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000036 |  |  |  |  | Date: | 05/03/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.9 | 21.8
|  | (Q) | 0.878 | 0.878 |  | 0.878 | 0.878
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.881 |  |  | 0.881
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.883
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 19 | 19 |  | 19 | 19
|  | (Q) | 2.22 | 2.22 |  | 2.22 | 2.23
D1 & D2 |  | (L) | 38.1 | mH |  | 38.1 | mH
|  | (Q) | 2.22 |  |  | 2.23
Magnet |  |  | (L) | 76.2 | mH
|  |  | (Q) | 2.23
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 4.41 | 4.39 |  | 4.51 | 4.54
|  | (Q) | 0.67 | 0.671 |  | 0.695 | 0.715
D1 & D2 |  | (L) | 8.79 | mH |  | 8.99 | mH
|  | (Q) | 0.666 |  |  | 0.699
Magnet |  |  | (L) | 17.8 | mH
|  |  | (Q) | 0.681
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000036 |  |  |  |  | Date: | 05/03/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 57.7 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 46.8 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 27.3 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 23.4 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 34 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 28.4 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.3 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.3 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.4 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.852 | 0.872 |  | 0.886 | 0.892
| Dipoles D1 & D2 [4KV] |  | 1.78 | mS |  | 1.78 | mS
| Magnet [4KV] |  |  | 2.73 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 375 | 398 | µS | 402 | 404 | µS
| [C= 2µF] | Current | 38.5 | 36 | A | 37.5 | 34.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION