## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F301 |  |  |  | YT111 | 20.7883 | Magnet | 5.97 | 5970.024 | 5981.988 | 10 | 0.876 | 21.9 |  | 0.876 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F301 |  |  |  | YT112 | 20.8239 | Aperture1 | 2.985 | 2984.981 | 2990.9629 | 100 | 2.18 | 18.9 |  | 2.19 | 18.9
[9 empty] | YT121 | 20.8561 | Aperture2 | 2.985 | 2985.029 | 2985.029 | 1000 | 0.671 | 4.33 |  | 0.698 | 4.43
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.075 | Apt1 Pup | 1.4929 | 1492.916 | 1495.9078
CERN PART NUMBER : |  |  | HCMBB_A00101 |  | Serial Number : |  | 000038 |  | YT211 | 21.2911 | Apt1 Plw | 1.492 | 1492.044 | 1495.0341 | 10 | 0.876 | 21.8 |  | 0.876 | 21.9
[9 empty] | YT212 | 21.4379 | Apt2 Pup | 1.493 | 1492.981 | 1495.9729 | 100 | 2.18 | 18.9 |  | 2.19 | 18.9
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.9728 | Apt2 Plw | 1.492 | 1492.027 | 1495.017 | 1000 | 0.675 | 4.33 |  | 0.714 | 4.44
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.8794
[15 empty] | 10 | 0.879 | 43.7 |  | 0.879 | 43.7
NAME OF TEST OPERATOR: |  |  | JARDOT | [11 empty] | 100 | 2.18 | 37.8 |  | 2.19 | 37.8
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.668 | 8.62 |  | 0.701 | 8.83
DATE OF TEST : |  |  | 03/04/2003 |  | TIME :
[15 empty] | 10 | 0.88 | 87.5
[15 empty] | 100 | 2.18 | 75.8
[15 empty] | 1000 | 0.682 | 17.4
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 32 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1492.916 | 1492.044 |  | 1492.981 | 1492.027
Poles [20°C] |  |  | 1495.9078 | 1495.0341 |  | 1495.9729 | 1495.017
D1 & D2 |  |  | 2990.9629 | mW |  | 2985.029 | mW
Magnet |  |  |  | 5981.988 | mW
|  | Poles Nr. | JP149 | JP150 |  | JP151 | JP152
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 20.7883 | 20.8561 |  | 21.2911 | 20.9728
|  |  | 20.8239 | 21.075 |  | 21.4379 | 20.8794
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 190 | nF |  | 180 | nF
D1 & D2 -----> Ground |  |  | 180 | nF |  | 180 | nF
Magnet -----> Ground |  |  |  | 280 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000038 |  |  |  |  | Date: | 03/04/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.8 |  | 21.9 | 21.9
|  | (Q) | 0.876 | 0.876 |  | 0.876 | 0.876
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.879 |  |  | 0.879
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.88
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 18.9 | 18.9 |  | 18.9 | 18.9
|  | (Q) | 2.18 | 2.18 |  | 2.18 | 2.19
D1 & D2 |  | (L) | 37.8 | mH |  | 37.8 | mH
|  | (Q) | 2.18 |  |  | 2.19
Magnet |  |  | (L) | 75.8 | mH
|  |  | (Q) | 2.18
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 4.33 | 4.33 |  | 4.43 | 4.44
|  | (Q) | 0.671 | 0.675 |  | 0.698 | 0.714
D1 & D2 |  | (L) | 8.62 | mH |  | 8.83 | mH
|  | (Q) | 0.668 |  |  | 0.701
Magnet |  |  | (L) | 17.4 | mH
|  |  | (Q) | 0.682
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000038 |  |  |  |  | Date: | 03/04/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 57.5 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 58.5 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 26.8 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 27 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 38.8 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 37.6 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.3 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.4 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.4 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.6 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.85 | 0.848 |  | 0.876 | 0.876
| Dipoles D1 & D2 [4KV] |  | 1.77 | mS |  | 1.78 | mS
| Magnet [4KV] |  |  | 2.72 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 411 | 413 | µS | 418 | 419 | µS
| [C= 2µF] | Current | 37.5 | 37 | A | 36.5 | 36.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION