## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 20.9008 | Magnet | 5.9817 | 5981.746 | 6005.7691 | 10 | 0.875 | 21.8 |  | 0.876 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 21.0025 | Aperture1 | 2.9914 | 2991.384 | 3003.3976 | 100 | 2.21 | 19 |  | 2.21 | 19
[9 empty] | YT121 | 20.9478 | Aperture2 | 2.9904 | 2990.354 | 3002.3635 | 1000 | 0.672 | 4.4 |  | 0.698 | 4.48
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 20.98 | Apt1 Pup | 1.4958 | 1495.774 | 1501.7811
CERN PART NUMBER : |  |  | HCMBB_A00101 |  | Serial Number : |  | 000040 |  | YT211 | 21.1698 | Apt1 Plw | 1.4956 | 1495.602 | 1501.6084 | 10 | 0.874 | 21.8 |  | 0.874 | 21.8
[9 empty] | YT212 | 21.0626 | Apt2 Pup | 1.495 | 1494.954 | 1500.9578 | 100 | 2.2 | 18.9 |  | 2.21 | 18.9
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.8635 | Apt2 Plw | 1.4954 | 1495.381 | 1501.3865 | 1000 | 0.675 | 4.39 |  | 0.717 | 4.51
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.819
[15 empty] | 10 | 0.878 | 43.7 |  | 0.878 | 43.7
NAME OF TEST OPERATOR: |  |  | JARDOT | [11 empty] | 100 | 2.21 | 38 |  | 2.21 | 37.9
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.67 | 8.75 |  | 0.704 | 8.98
DATE OF TEST : |  |  | 16/05/2003 |  | TIME :
[15 empty] | 10 | 0.88 | 87.5
[15 empty] | 100 | 2.21 | 76
[15 empty] | 1000 | 0.687 | 17.7
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 35 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1495.774 | 1495.602 |  | 1494.954 | 1495.381
Poles [20°C] |  |  | 1501.7811 | 1501.6084 |  | 1500.9578 | 1501.3865
D1 & D2 |  |  | 3003.3976 | mW |  | 3002.3635 | mW
Magnet |  |  |  | 6005.7691 | mW
|  | Poles Nr. | JP157 | JP158 |  | JP159 | JP160
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 20.9008 | 20.9478 |  | 21.1698 | 20.8635
|  |  | 21.0025 | 20.98 |  | 21.0626 | 20.819
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 190 | nF |  | 190 | nF
D1 & D2 -----> Ground |  |  | 180 | nF |  | 180 | nF
Magnet -----> Ground |  |  |  | 280 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000040 |  |  |  |  | Date: | 16/05/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.9 | 21.8
|  | (Q) | 0.875 | 0.874 |  | 0.876 | 0.874
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.878 |  |  | 0.878
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.88
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 19 | 18.9 |  | 19 | 18.9
|  | (Q) | 2.21 | 2.2 |  | 2.21 | 2.21
D1 & D2 |  | (L) | 38 | mH |  | 37.9 | mH
|  | (Q) | 2.21 |  |  | 2.21
Magnet |  |  | (L) | 76 | mH
|  |  | (Q) | 2.21
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 4.4 | 4.39 |  | 4.48 | 4.51
|  | (Q) | 0.672 | 0.675 |  | 0.698 | 0.717
D1 & D2 |  | (L) | 8.75 | mH |  | 8.98 | mH
|  | (Q) | 0.67 |  |  | 0.704
Magnet |  |  | (L) | 17.7 | mH
|  |  | (Q) | 0.687
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000040 |  |  |  |  | Date: | 16/05/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 45.2 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 51 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 19.8 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 27.8 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 38.6 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 43.4 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.3 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.4 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 860 | 854 |  | 862 | 866
| Dipoles D1 & D2 [4KV] |  | 1.78 | mS |  | 1.78 | mS
| Magnet [4KV] |  |  | 2.69 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 423 | 407 | µS | 431 | 431 | µS
| [C= 2µF] | Current | 38 | 38.5 | A | 36.5 | 38.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION